## Summary
Point of Access Capacity Factor |  | Point of Access Irriadiation Capacity Factor | Electricity Production Capacity Factor | Performance Ratio
| EU Data | 22.9% | 17.12% | 74.78%
| PVWatts | 22.49% | 16.69% | 74.24%
| PVSYST | 23.28% | 18.94% | 81.36%
| Helioscope | 20.92% | 16.37% | 78.25%
Percent Difference (High/Low) |  | 11.3% | 15.72% | 7.121%
Importance of PR
| Capcity Factor from Collector |  |  | 23%
| PR Low |  |  | 74.24%
| Final Capacity Factor |  |  | 17.07%
| PR High |  |  | 81.36%
| Final Capacity Factor |  |  | 18.71%
| Percent Difference in Capacity Factor |  |  | 9.592%
| DSCR Effect |  |  | 1.1061

## EU Summary
Summary of Annual
| Month | Em: Average monthly electricity production from the given system [kWh]. | Hm: Average monthly sum of global irradiation per square meter received by the modules of the given system [kWh/m²]. | SDm: Standard deviation of the monthly electricity production due to year-to-year variation [kWh].
| January | 114 | 150 | 5.8 |  | Em: Average monthly electricity production from the given system [kWh].
| February | 122 | 161 | 10.8 |  | Hm: Average monthly sum of global irradiation per square meter received by the modules of the given system [kWh/m²].
| March | 145 | 192 | 7.35 |  | SDm: Standard deviation of the monthly electricity production due to year-to-year variation [kWh].
| April | 142 | 192 | 10.1
| May | 137 | 186 | 8.19
| June | 117 | 158 | 4.84
| July | 127 | 172 | 5.91
| August | 128 | 173 | 7.98
| September | 115 | 156 | 13.6
| October | 124 | 165 | 9.01
| November | 114 | 150 | 7.6
| December | 115 | 151 | 9.2
|  | 1500 | 2006
| Cap Fac | 17.12% | 22.9%
| Performance Ratio |  | 74.78%
Monthly energy output from tracking PV system:
[5 empty] | January | February | March | April | May | June | July | August | September | October | November | December | Total
Vertical Axis
Month Em Hm SDm
| Em: kWh |  |  |  | 154 | 164 | 193 | 191 | 190 | 154 | 168 | 168 | 150 | 158 | 151 | 153 | 1994 | 22.76%
| Hm: kWh/m2 |  |  |  | 202 | 215 | 254 | 253 | 254 | 205 | 224 | 225 | 200 | 210 | 198 | 201 | 2641 | 30.15%
[5 empty] | 9.97 | 18.1 | 8.77 | 10.9 | 17 | 11.6 | 11.2 | 9.48 | 20.4 | 10.5 | 13.2 | 14.7
Inclined Axis
Em Hm SDm
| Em: kWh |  |  |  | 152 | 166 | 200 | 199 | 195 | 154 | 170 | 174 | 156 | 161 | 148 | 148 | 2023 | 23.09%
| Hm: kWh/m2 |  |  |  | 198 | 217 | 264 | 265 | 260 | 205 | 227 | 233 | 209 | 214 | 194 | 193 | 2679 | 30.58%
[5 empty] | 9.54 | 18 | 9.04 | 11.5 | 17.5 | 11.6 | 11.3 | 9.98 | 21.3 | 10.7 | 12.8 | 13.9
Two Axis
Em Hm SDm
| Em: kWh |  |  |  | 160 | 169 | 201 | 201 | 203 | 164 | 179 | 178 | 156 | 163 | 154 | 158 | 2086 | 23.81%
| Hm: kWh/m2 |  |  |  | 209 | 222 | 265 | 268 | 272 | 219 | 240 | 239 | 210 | 216 | 203 | 207 | 2770 | 31.62% | 75.31%
[5 empty] | 10.5 | 18.9 | 9.09 | 11.6 | 18.4 | 12.6 | 12 | 10.1 | 21.3 | 11 | 13.6 | 15.5

## pvwatts_monthly (2)
PVWatts: Monthly PV Performance Data
Requested Location: | cancun
Location: | LA BAJADA, CUBA
Lat (deg N): | 21.92
Long (deg W): | 84.47
Elev (m): | 4
DC System Size (kW): | 1
Module Type: | Standard
Array Type: | Fixed (open rack)
Array Tilt (deg): | 21.2
Array Azimuth (deg): | 180
System Losses: | 14
Invert Efficiency: | 96
DC to AC Size Ratio: | 1.1
Average Cost of Electricity Purchased from Utility ($/kWh): | No utility data available
Capacity Factor (%) | 16.7
Month | AC System Output(kWh) | Solar Radiation (kWh/m^2/day) | Plane of Array Irradiance (W/m^2) | DC array Output (kWh) | Value ($)
1 | 117.0386 | 5.0106 | 155.3299 | 122.2026 | 0
2 | 113.7653 | 5.4056 | 151.3573 | 118.7914 | 0
3 | 138.409 | 5.8794 | 182.2609 | 144.421 | 0
4 | 133.9987 | 5.9829 | 179.4868 | 139.9088 | 0
5 | 130.4309 | 5.6566 | 175.3545 | 136.23 | 0
6 | 120.4284 | 5.451 | 163.5294 | 125.8751 | 0
7 | 128.35 | 5.7387 | 177.9006 | 134.1347 | 0
8 | 126.4604 | 5.6176 | 174.1452 | 132.1312 | 0
9 | 121.4986 | 5.5274 | 165.8212 | 126.9768 | 0
10 | 117.0601 | 5.1307 | 159.0514 | 122.2832 | 0
11 | 112.384 | 4.9955 | 149.864 | 117.2896 | 0
12 | 102.5753 | 4.38 | 135.7806 | 107.1977 | 0
Total | 1462.3992 | 64.776 | 1969.8818 | 1527.4422 | 0
Cap Factor | 16.69% |  | 22.49%
Performance Ratio | 74.24%

## Global IR
Month | January | February | March | April | May | June | July | August | September | October | November | December | Total | Capactiy Factor
2005 | 177 | 164 | 200 | 186 | 179 | 153 | 177 | 170 | 157 | 153 | 153 | 161 | 2030 | 23.17%
2006 | 160 | 160 | 194 | 202 | 173 | 160 | 171 | 162 | 169 | 161 | 137 | 128 | 1977 | 22.57%
2007 | 154 | 148 | 178 | 190 | 188 | 160 | 181 | 163 | 167 | 163 | 153 | 152 | 1997 | 22.8%
2008 | 148 | 161 | 188 | 199 | 191 | 150 | 176 | 191 | 152 | 151 | 159 | 149 | 2015 | 23%
2009 | 158 | 177 | 189 | 203 | 199 | 169 | 185 | 173 | 162 | 170 | 146 | 147 | 2078 | 23.72%
2010 | 135 | 130 | 198 | 163 | 190 | 166 | 165 | 179 | 171 | 182 | 158 | 155 | 1992 | 22.74%
2011 | 151 | 155 | 201 | 203 | 209 | 148 | 172 | 166 | 168 | 143 | 157 | 162 | 2035 | 23.23%
2012 | 147 | 157 | 190 | 181 | 168 | 158 | 174 | 188 | 108 | 171 | 148 | 164 | 1954 | 22.31%
2013 | 144 | 161 | 176 | 190 | 194 | 157 | 167 | 165 | 145 | 161 | 138 | 143 | 1941 | 22.16%
2014 | 139 | 177 | 209 | 206 | 180 | 172 | 173 | 181 | 153 | 163 | 156 | 159 | 2068 | 23.61%
2015 | 152 | 163 | 189 | 191 | 202 | 159 | 183 | 176 | 161 | 159 | 144 | 141 | 2020 | 23.06%
| November: Standard Deviation | 43.1465 | 0.4925%
| June: % = (DSCR-1)/DSCR; November: Average | 2009.7273 | 22.94%
| June: DSCR x % = DSCR - 1; November: Std Dev/Avearage | 2.147% | 2.147%
DSCR x % - DSCR = -1
| June: DSCR - DSCR * % = 1; November: P90 |  | 20.19%
| June: DSCR = 1/(1-%); November: P90/P50 |  | 88.01%
| November: % Red |  | 11.99%
| November: DSCR - P90 |  | 1.1363

## PV Syst
GlobHor | DiffHor | T | Amb | GlobInc | GlobEff | EArray | E_Grid | PR
| kWh/m² | kWh/m² | °C | kWh/m² | kWh/m² | MWh | MWh
Enero | 127.6 | 55.45 | 21.68 | 165 | 161.7 | 13208 | 12977 | 0.834
Febrero | 137.2 | 55.9 | 23.04 | 164.2 | 160.8 | 12938 | 12710 | 0.821
Marzo | 181.1 | 66.23 | 24.87 | 196.3 | 191.9 | 15180 | 14910 | 0.805
Abril | 195.7 | 71.06 | 25.96 | 187.6 | 182.2 | 14525 | 14271 | 0.806
Mayo | 200.8 | 81.18 | 28.22 | 175.2 | 169.5 | 13567 | 13334 | 0.807
Junio | 181.5 | 89.59 | 28.28 | 153.9 | 148.6 | 12053 | 11847 | 0.816
Julio | 206 | 89.12 | 28.92 | 176.3 | 170.1 | 13652 | 13420 | 0.807
Agosto | 191.9 | 80.66 | 28.49 | 177.7 | 172.2 | 13684 | 13450 | 0.803
Septiembre | 164.1 | 69.18 | 26.9 | 168.2 | 163.8 | 12993 | 12767 | 0.805
Octubre | 141.4 | 70.22 | 26.19 | 161.1 | 157.1 | 12618 | 12399 | 0.816
Noviembre | 123.7 | 46.79 | 23.65 | 158.6 | 155.5 | 12446 | 12224 | 0.817
Diciembre | 115.4 | 47.07 | 22.55 | 155.2 | 152.1 | 12398 | 12180 | 0.832
Año | 1966.4 | 822.45 | 308.75 | 2039.3 | 1985.5 | 159262 | 156489 | 0.81359
Capacity | [5 empty] | 94319 | 94319
Yield (kWh/kWp) | [5 empty] | 1688.5463 | 1659.1461
Hours | 22.45% | 9.389% | 3.525% | 23.28% | 22.67% | 19.28% | 18.94% | 81.36%

## Helioscope
| kWh/m2 | Raw CF | PR | CF
With Tilt | 1832.3 | 20.92% | 78.2% | 16.36% | PR | 78.2% |  | 8760 |  | 0.82321
Raw | 1743.7 | 19.91% |  |  | kWp | 2640
[5 empty] | kWh/kWp | 1433.7
[5 empty] | CF | 16.37%
[5 empty] | 1743.7 | 19.91%
[5 empty] | 1832.3 | 20.92%
[5 empty] | 1790.9 | 20.44%
[5 empty] | 1737.2 | 19.83%
[5 empty] | 1702.5 | 19.43% |  |  |  | 0.97637
[5 empty] | kWh | kWp | kWh/kWp | CF
[5 empty] | 4489239 | 2640 | 1700.4693 | 19.41%
[5 empty] | 4356246 | 2640 | 1650.0932 | 18.84%
[5 empty] | 3999443 | 2640 | 1514.9405 | 17.29%
[5 empty] | 3907199 | 2640 | 1479.9996 | 16.89%
[5 empty] | 3884223 | 2640 | 1471.2966 | 16.8%
[5 empty] | 3881727 | 2640 | 1470.3511 | 16.78%
[5 empty] | 3804050 | 2640 | 1440.928 | 16.45%
[5 empty] | 3785030 | 2640 | 1433.7235 | 16.37% |  | 0.84313
[6 empty] | PR |  | 78.25% | 16.37%

## EU Raw Data
Latitude (decimal degrees): 21.268
Longitude (decimal degrees): -87.482
Radiation database: PVGIS-NSRDB
Nominal power of the PV system (crystalline silicon) (kWp): 1
System losses(%): 14
Fixed slope of modules (deg.) (optimum): 22
Orientation (azimuth) of modules (optimum): -17
Fixed angle
Month Ed Em Hd Hm SDm
1 3.69 114 4.85 150 5.80
2 4.34 122 5.74 161 10.8
3 4.67 145 6.20 192 7.35
4 4.75 142 6.38 192 10.1
5 4.44 137 6.00 186 8.19
6 3.90 117 5.27 158 4.84
7 4.09 127 5.56 172 5.91
8 4.11 128 5.59 173 7.98
9 3.84 115 5.20 156 13.6
10 4.00 124 5.34 165 9.01
11 3.79 114 4.99 150 7.60
12 3.70 115 4.86 151 9.20
Year 4.11 125 5.50 167 2.36
AOI loss (%) Spectral effects (%) Temperature and low irradiance loss (%) Combined losses (%)
Fixed system: 2.9 ?(0) 10.4 25.2
Ed: Average daily energy production from the given system (kWh)
Em: Average monthly energy production from the given system (kWh)
Hd: Average daily sum of global irradiation per square meter received by the modules of the given system (kWh/m2)
Hm: Average monthly sum of global irradiation per square meter received by the modules of the given system (kWh/m2)
SDm: Standard deviation of the monthly energy production due to year-to-year variation (kWh)
PVGIS (c) European Communities | 2001-2016

## Raw Tracking
Monthly energy output from tracking PV system:
January
February
March
April
May
June
July
August
September
October
November
December
Vertical Axis
Month Em Hm SDm
154
164
193
191
190
154
168
168
150
158
151
153
202
215
254
253
254
205
224
225
200
210
198
201
9.97
18.1
8.77
10.9
17
11.6
11.2
9.48
20.4
10.5
13.2
14.7
Inclined Axis
Em Hm SDm
152
166
200
199
195
154
170
174
156
161
148
148
198
217
264
265
260
205
227
233
209
214
194
193
9.54
18
9.04
11.5
17.5
11.6
11.3
9.98
21.3
10.7
12.8
13.9
Two Axis
Em Hm SDm
160
169
201
201
203
164
179
178
156
163
154
158
209
222
265
268
272
219
240
239
210
216
203
207
10.5
18.9
9.09
11.6
18.4
12.6
12
10.1
21.3
11
13.6
15.5

## Raw Monthly
Month
January
February
March
April
May
June
July
August
September
October
November
December
2005
177
164
200
186
179
153
177
170
157
153
153
161
2006
160
160
194
202
173
160
171
162
169
161
137
128
2007
154
148
178
190
188
160
181
163
167
163
153
152
2008
148
161
188
199
191
150
176
191
152
151
159
149
2009
158
177
189
203
199
169
185
173
162
170
146
147
2010
135
130
198
163
190
166
165
179
171
182
158
155
2011
151
155
201
203
209
148
172
166
168
143
157
162
2012
147
157
190
181
168
158
174
188
108
171
148
164
2013
144
161
176
190
194
157
167
165
145
161
138
143
2014
139
177
209
206
180
172
173
181
153
163
156
159
2015
152
163
189
191
202
159
183
176
161
159
144
141