## Introduction
This exercise is to make you work through incremental heat rate curves
Begin by getting data from the List -- Use Index and Combo Box
Make table with different capacity levels
Compute Energy Used (BTU or Kcal) from the quadractic equation

## Tech_Data_Revised
Code | English Name | Plant Type | Capacity MW | Min Output MW |  |  | Max Output | Ramp Up Rate MW/Hour | Ramp Down Rate | Min Up Time Hours | Min Down Time Hours | Heat Cost(kcal/kg,l) |  | Fuel Price (Won/Gcal) | Square Term | Linear Term | Constant | MOR - Scheduled Maintenance Days | EFOR - Equivalent Forced Outage Rate | Scheduled Maintenace Percent | Forced Outage Percent | Total Maintenace Outage | Fuel Cost per kWh | Adj Fuel Cost | Heat Rate | Full Load Heat Rate kCal/kWh
1010 | Hwacheon | Hyrdro | 108 | 10 | 30 | 50 | 70 | 70 | 70 | 1 | 1 | 0 | 285.9177 | 0 | 0.016096 | 0.82495 | 9.0798 | 24 | 1 | 6.575% | 1% | 7.575% | 0 | 4.5599e-06 | 1361.9701 | 2647.3862
1020 | Chuncheon | Hyrdro | 57.6 | 10 | 26 | 42 | 58 | 58 | 58 | 1 | 1 | 0 | 229.2315 | 0 | 0.007642 | 3.4324 | 6.1714 | 21 | 1 | 5.753% | 1% | 6.753% | 0 | 2.9307e-06 | 925.7122 | 3979.7138
1030 | Uiam | Hyrdro | 45 | 10 | 21.6667 | 33.3333 | 45 | 45 | 45 | 1 | 1 | 0 | 351.0056 | 0 | 0.036842 | 5.9478 | 8.748 | 33 | 1 | 9.041% | 1% | 10.04% | 0 | 4.4825e-06 | 1312.2052 | 7800.1238
1040 | Cheongpyong | Hyrdro | 79.6 | 10 | 33.3333 | 56.6667 | 80 | 80 | 80 | 1 | 1 | 0 | 376.8135 | 0 | 0.00053 | 4.6888 | 0.22327 | 10 | 1 | 2.74% | 1% | 3.74% | 0 | 5.0694e-06 | 33.4911 | 4733.8379
1050 | Paldang | Hyrdro | 120 | 20 | 53.3333 | 86.6667 | 120 | 120 | 120 | 1 | 1 | 0 | 2630.0077 | 0 | 0.0768 | 12.6329 | 8.1392 | 20 | 1 | 5.479% | 1% | 6.479% | 0 | 8.3514e-06 | 1220.8844 | 21916.7309
1060 | kanglung | Hyrdro | 82 | 20 | 40.6667 | 61.3333 | 82 | 82 | 82 | 1 | 1 | 0 | 15.9509 | 0 | 0.000342 | 0.16266 | 0.31328 | 16 | 1 | 4.384% | 1% | 5.384% | 0 | 1.5339e-06 | 46.9914 | 194.5234
1070 | Soyangkang | Hyrdro | 200 | 50 | 100 | 150 | 200 | 45 | 45 | 1 | 1 | 0 | 268.5762 | 0 | 0.002351 | 0.76356 | 21.824 | 20 | 1 | 5.479% | 1% | 6.479% | 0 | 6.3583e-06 | 3273.6035 | 1342.8811
1080 | Choongju | Hyrdro | 412 | 50 | 170.6667 | 291.3333 | 412 | 200 | 200 | 1 | 1 | 0 | 695.174 | 0 | 0.000544 | 1.4001 | 25.9756 | 20 | 1 | 5.479% | 1% | 6.479% | 0 | 6.7534e-06 | 3896.3447 | 1687.3156
1090 | Daecheong | Hyrdro | 90 | 23 | 45.3333 | 67.6667 | 90 | 45 | 45 | 1 | 1 | 0 | 217.3882 | 0 | 0.001362 | 1.995 | 26.8042 | 20 | 1 | 5.479% | 1% | 6.479% | 0 | 7.6212e-06 | 4020.6263 | 2415.4242
1100 | Andong | Hyrdro | 90 | 23 | 45.3333 | 67.6667 | 90 | 45 | 45 | 1 | 1 | 0 | 184.0835 | 0 | 0.002143 | 1.7889 | 5.7274 | 20 | 1 | 5.479% | 1% | 6.479% | 0 | 9.7092e-06 | 859.1122 | 2045.3719
1110 | Habcheon | Hyrdro | 101.2 | 34 | 56 | 78 | 100 | 50 | 50 | 1 | 1 | 0 | 126.4088 | 0 | 0.003653 | 0.80215 | 7.819 | 20 | 1 | 5.479% | 1% | 6.479% | 0 | 6.0999e-06 | 1172.8446 | 1249.0991
1120 | Imha | Hyrdro | 50 | 13 | 25.3333 | 37.6667 | 50 | 25 | 25 | 1 | 1 | 0 | 9.3012 | 0 | 0.000342 | 0.16266 | 0.31328 | 20 | 1 | 5.479% | 1% | 6.479% | 0 | 8.9974e-06 | 46.9914 | 186.0245
1140 | Sumjinkang | Hyrdro | 34.8 | 8 | 16.6667 | 25.3333 | 34 | 34 | 34 | 1 | 1 | 0 | 31.9641 | 0 | 0.001517 | 0.86172 | 0.13924 | 16 | 1 | 4.384% | 1% | 5.384% | 0 | 5.9491e-06 | 20.8859 | 918.5077
1170 | Juam | Hyrdro | 23 | 6 | 11.6667 | 17.3333 | 23 | 11.2 | 11.2 | 1 | 1 | 0 | 20.7612 | 0 | 0.001517 | 0.86172 | 0.13924 | 20 | 1 | 5.479% | 1% | 6.479% | 0 | 7.8489e-06 | 20.8859 | 902.6599
1190 | Yongdam#1 | Hyrdro | 22.1 | 3 | 9.3333 | 15.6667 | 22 | 11.1 | 11.1 | 1 | 1 | 0 | 8.5044 | 0 | 7.7e-05 | 0.32718 | 1.2361 | 20 | 1 | 5.479% | 1% | 6.479% | 0 | 6.5168e-06 | 185.4108 | 384.8146
1610 | MujuPS | Pumped Storage | 600 | 210 | 340 | 470 | 600 | 100 | 100 | 0.5 | 1 | 0 | 140.9254 | 0 | 0.000221 | 0.071029 | 18.748 | 20 | 1 | 5.479% | 1% | 6.479% | 0 | 3.5994e-06 | 2812.2058 | 234.8757
1620 | SamlangjinPS | Pumped Storage | 600 | 200 | 333.3333 | 466.6667 | 600 | 200 | 200 | 0.5 | 1 | 0 | 221.6577 | 0 | 0.000291 | 0.1519 | 25.7577 | 26 | 1.5 | 7.123% | 1.5% | 8.623% | 0 | 1.9687e-06 | 3863.6506 | 369.4295
1630 | CheongpyongPS | Pumped Storage | 400 | 120 | 213.3333 | 306.6667 | 400 | 80 | 80 | 0.5 | 0.5 | 0 | 124.2354 | 0 | 0.000405 | 0.12085 | 11.097 | 39 | 1.5 | 10.68% | 1.5% | 12.18% | 0 | 6.6323e-06 | 1664.5466 | 310.5884
1650 | SancheongPS | Pumped Storage | 700 | 200 | 366.6667 | 533.3333 | 700 | 150 | 150 | 0.5 | 1 | 0 | 260.3135 | 0 | 0.000333 | 0.099799 | 27.2842 | 41 | 1.5 | 11.23% | 1.5% | 12.73% | 0 | 7.8976e-06 | 4092.6355 | 371.8765
2031 | Seoincheon1CC#1 | CC | 225 | 175 | 191.3333 | 207.6667 | 224 | 11.7 | 11.7 | 4 | 3 | 12999 | 407.8819 | 30.854 | 0.001209 | 1.0958 | 100.117 | 38 | 6.5 | 10.41% | 6.5% | 16.91% | 55.9324 | 55.9324 | 15017.5457 | 1812.8083
2032 | Seoincheon1CC#2 | CC | 225 | 175 | 191.3333 | 207.6667 | 224 | 11.7 | 11.7 | 4 | 3 | 13000 | 407.8819 | 30.854 | 0.001209 | 1.0958 | 100.117 | 38 | 6.5 | 10.41% | 6.5% | 16.91% | 55.9324 | 55.9324 | 15017.5457 | 1812.8083
2033 | Seoincheon1CC#3 | CC | 225 | 175 | 191.3333 | 207.6667 | 224 | 11.7 | 11.7 | 4 | 3 | 13001 | 407.8819 | 30.854 | 0.001209 | 1.0958 | 100.117 | 38 | 6.5 | 10.41% | 6.5% | 16.91% | 55.9324 | 55.9324 | 15017.5457 | 1812.8083
2034 | Seoincheon1CC#4 | CC | 225 | 175 | 191.3333 | 207.6667 | 224 | 11.7 | 11.7 | 4 | 3 | 13002 | 407.8819 | 30.854 | 0.001209 | 1.0958 | 100.117 | 38 | 6.5 | 10.41% | 6.5% | 16.91% | 55.9324 | 55.9324 | 15017.5457 | 1812.8083
2061 | Seoincheon1CC#5 | CC | 225 | 175 | 191.3333 | 207.6667 | 224 | 11.7 | 11.7 | 4 | 3 | 12999 | 407.8819 | 30.854 | 0.001209 | 1.0958 | 100.117 | 38 | 6.5 | 10.41% | 6.5% | 16.91% | 55.9324 | 55.9324 | 15017.5457 | 1812.8083
2062 | Seoincheon1CC#6 | CC | 225 | 175 | 191.3333 | 207.6667 | 224 | 11.7 | 11.7 | 4 | 3 | 13000 | 407.8819 | 30.854 | 0.001209 | 1.0958 | 100.117 | 38 | 6.5 | 10.41% | 6.5% | 16.91% | 55.9324 | 55.9324 | 15017.5457 | 1812.8083
2063 | Seoincheon1CC#7 | CC | 225 | 175 | 191.3333 | 207.6667 | 224 | 11.7 | 11.7 | 4 | 3 | 13001 | 407.8819 | 30.854 | 0.001209 | 1.0958 | 100.117 | 38 | 6.5 | 10.41% | 6.5% | 16.91% | 55.9324 | 55.9324 | 15017.5457 | 1812.8083
2064 | Seoincheon1CC#8 | CC | 225 | 175 | 191.3333 | 207.6667 | 224 | 11.7 | 11.7 | 4 | 3 | 13002 | 407.8819 | 30.854 | 0.001209 | 1.0958 | 100.117 | 38 | 6.5 | 10.41% | 6.5% | 16.91% | 55.9324 | 55.9324 | 15017.5457 | 1812.8083
2091 | Shinincheon2CC#9 | CC | 450 | 165 | 275.6667 | 386.3333 | 497 | 25 | 25 | 4 | 3 | 12999 | 782.9142 | 30.854 | 1e-06 | 1.6426 | 43.5606 | 49 | 6.5 | 13.42% | 6.5% | 19.92% | 53.6801 | 53.6801 | 6534.0927 | 1739.8094
2092 | Shinincheon2CC#10 | CC | 450 | 165 | 275.6667 | 386.3333 | 497 | 25 | 25 | 4 | 3 | 13000 | 782.9142 | 30.854 | 1e-06 | 1.6426 | 43.5606 | 49 | 6.5 | 13.42% | 6.5% | 19.92% | 53.6801 | 53.6801 | 6534.0927 | 1739.8094
2121 | Shinincheon2CC#11 | CC | 450 | 165 | 275.6667 | 386.3333 | 497 | 25 | 25 | 4 | 3 | 12999 | 782.9142 | 30.854 | 1e-06 | 1.6426 | 43.5606 | 49 | 6.5 | 13.42% | 6.5% | 19.92% | 53.6801 | 53.6801 | 6534.0927 | 1739.8094
2122 | Shinincheon2CC#12 | CC | 450 | 165 | 275.6667 | 386.3333 | 497 | 25 | 25 | 4 | 3 | 13000 | 782.9142 | 30.854 | 1e-06 | 1.6426 | 43.5606 | 49 | 6.5 | 13.42% | 6.5% | 19.92% | 53.6801 | 53.6801 | 6534.0927 | 1739.8094
2211 | AnyangCC#1 | CC | 450 | 180 | 275.6667 | 371.3333 | 467 | 22.5 | 22.5 | 4 | 3 | 12999 | 892.6805 | 30.854 | 0.000203 | 1.8374 | 24.7291 | 45 | 6.5 | 12.33% | 6.5% | 18.83% | 61.2061 | 61.2062 | 3709.362 | 1983.7345
2271 | BundangCC#1 | CC | 560 | 180 | 304.3333 | 428.6667 | 553 | 12 | 12 | 4 | 3 | 13019 | 1191.4561 | 30.854 | 3e-06 | 2.0119 | 63.8284 | 36 | 6.5 | 9.863% | 6.5% | 16.36% | 65.645 | 65.645 | 9574.2584 | 2127.6003
2272 | BundangCC#2 | CC | 340 | 105 | 186.3333 | 267.6667 | 349 | 12 | 12 | 4 | 3 | 13019 | 696.5278 | 30.854 | 0.000238 | 1.5955 | 126.5576 | 47 | 6.5 | 12.88% | 6.5% | 19.38% | 63.2079 | 63.2079 | 18983.6439 | 2048.6113
2311 | IlsanCC#1 | CC | 600 | 221 | 353 | 485 | 617 | 45 | 45 | 4 | 3 | 12999 | 1169.1826 | 30.854 | 1e-06 | 1.877 | 42.6178 | 38 | 6.5 | 10.41% | 6.5% | 16.91% | 60.1233 | 60.1233 | 6392.6646 | 1948.6376
2312 | IlsanCC#2 | CC | 300 | 111 | 178 | 245 | 312 | 25 | 25 | 4 | 3 | 12999 | 569.3804 | 30.854 | 0.000286 | 1.3348 | 143.2025 | 25 | 6.5 | 6.849% | 6.5% | 13.35% | 58.5589 | 58.5589 | 21480.3762 | 1897.9347
2341 | BucheonCC#1 | CC | 450 | 155 | 259.6667 | 364.3333 | 469 | 27.6 | 27.6 | 3 | 3 | 12999 | 893.3464 | 30.854 | 0.000905 | 1.0701 | 228.5425 | 45 | 6.5 | 12.33% | 6.5% | 18.83% | 61.2518 | 61.2518 | 34281.3732 | 1985.2142
2381 | PyongtackCC#1 | CC | 480 | 163 | 275.3333 | 387.6667 | 500 | 43.2 | 43.2 | 4 | 3 | 12999 | 970.2293 | 30.854 | 0.000167 | 1.7656 | 84.2568 | 36 | 6.5 | 9.863% | 6.5% | 16.36% | 62.3655 | 62.3655 | 12638.5234 | 2021.311
2431 | UlsanCC#1 | CC | 300 | 100 | 167.3333 | 234.6667 | 302 | 15 | 15 | 4 | 3 | 12999 | 598.1898 | 30.854 | 1e-06 | 1.8531 | 42.1602 | 34 | 6.5 | 9.315% | 6.5% | 15.82% | 61.5218 | 61.5218 | 6324.0289 | 1993.966
2432 | UlsanCC#2 | CC | 450 | 165 | 280.3333 | 395.6667 | 511 | 20 | 20 | 4 | 3 | 12999 | 795.7224 | 30.854 | 1e-06 | 1.6093 | 71.3246 | 39 | 6.5 | 10.68% | 6.5% | 17.18% | 54.5583 | 54.5583 | 10698.6827 | 1768.272
2433 | UlsanCC#3 | CC | 450 | 165 | 280.3333 | 395.6667 | 511 | 20 | 20 | 4 | 3 | 13000 | 795.7224 | 30.854 | 1e-06 | 1.6093 | 71.3246 | 35 | 6.5 | 9.589% | 6.5% | 16.09% | 54.5583 | 54.5583 | 10698.6827 | 1768.272
2481 | BoryeongCC#1 | CC | 450 | 196 | 297 | 398 | 499 | 21 | 21 | 4 | 3 | 12999 | 732.9027 | 30.854 | 2e-06 | 1.5352 | 41.655 | 38 | 10 | 10.41% | 10% | 20.41% | 50.2511 | 50.2511 | 6248.2459 | 1628.6726
2482 | BoryeongCC#2 | CC | 450 | 196 | 297 | 398 | 499 | 21 | 21 | 4 | 3 | 13000 | 732.9027 | 30.854 | 2e-06 | 1.5352 | 41.655 | 38 | 10 | 10.41% | 10% | 20.41% | 50.2511 | 50.2511 | 6248.2459 | 1628.6726
2483 | BoryeongCC#3 | CC | 450 | 196 | 297 | 398 | 499 | 21 | 21 | 4 | 3 | 13001 | 732.9027 | 30.854 | 2e-06 | 1.5352 | 41.655 | 38 | 10 | 10.41% | 10% | 20.41% | 50.2511 | 50.2511 | 6248.2459 | 1628.6726
2484 | BoryeongCC#4 | CC | 450 | 196 | 297 | 398 | 499 | 21 | 21 | 4 | 3 | 13002 | 732.9027 | 30.854 | 2e-06 | 1.5352 | 41.655 | 38 | 10 | 10.41% | 10% | 20.41% | 50.2511 | 50.2511 | 6248.2459 | 1628.6726
2551 | HanhwaCC#1 | CC | 450 | 130 | 230.6667 | 331.3333 | 432 | 22 | 22 | 4 | 1 | 12999 | 932.7026 | 30.854 | 0.001871 | 0.52639 | 316.9501 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 63.9502 | 63.9502 | 47542.5094 | 2072.6725
2552 | HanhwaCC#2 | CC | 450 | 130 | 230.6667 | 331.3333 | 432 | 22 | 22 | 4 | 1 | 13000 | 932.7026 | 30.854 | 0.001871 | 0.52639 | 316.9501 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 63.9502 | 63.9502 | 47542.5094 | 2072.6725
2553 | HanhwaCC#3 | CC | 450 | 137 | 243 | 349 | 455 | 22 | 22 | 4 | 1 | 12999 | 853.3979 | 30.854 | 0.000814 | 1.0329 | 223.7386 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 58.5128 | 58.5128 | 33560.783 | 1896.4398
2554 | HanhwaCC#4 | CC | 450 | 137 | 243 | 349 | 455 | 22 | 22 | 4 | 1 | 13000 | 853.3979 | 30.854 | 0.000814 | 1.0329 | 223.7386 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 58.5128 | 58.5128 | 33560.783 | 1896.4398
2581 | BugokCC#1 | CC | 500 | 164 | 292 | 420 | 548 | 7.5 | 10 | 4 | 3 | 12999 | 849.7584 | 30.854 | 1e-06 | 1.6321 | 33.4749 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 52.4369 | 52.4369 | 5021.2305 | 1699.5167
2591 | Mokdong#1 | CC | 21 | 3 | 8.3333 | 13.6667 | 19 | 3.5 | 3.5 | 4 | 4 | 13000 | 61.4017 | 33.617 | 0.020887 | 1.7468 | 15.5083 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 98.2924 | 98.2925 | 2326.2405 | 2923.891
2601 | Nowon#1 | CC | 37 | 2 | 10.6667 | 19.3333 | 28 | 6.1 | 6.1 | 4 | 4 | 13000 | 117.5566 | 28.534 | 0.002553 | 2.9986 | 3.1143 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 90.6584 | 90.6584 | 467.1463 | 3177.2045
2631 | PusanCC1 | CC | 450 | 175 | 296.6667 | 418.3333 | 540 | 27.5 | 27.5 | 4 | 3 | 12999 | 757.6214 | 30.854 | 0.0001 | 1.5177 | 54.4248 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 51.9459 | 51.9459 | 8163.7202 | 1683.603
2632 | PusanCC2 | CC | 450 | 175 | 296.6667 | 418.3333 | 540 | 27.5 | 27.5 | 4 | 3 | 12999 | 757.6214 | 30.854 | 0.0001 | 1.5177 | 54.4248 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 51.9459 | 51.9459 | 8163.7202 | 1683.603
3014 | Seoul#4 | Oil | 137.5 | 56 | 81.3333 | 106.6667 | 132 | 2 | 2 | 6 | 12 | 12999 | 349.4254 | 30.854 | 0.00303 | 1.7861 | 46.5559 | 44 | 3 | 12.05% | 3% | 15.05% | 78.4085 | 78.4085 | 6983.3892 | 2541.2756
3015 | Seoul#5 | Oil | 250 | 115 | 158.3333 | 201.6667 | 245 | 3 | 3 | 7 | 12 | 12999 | 605.5434 | 30.854 | 0.002225 | 1.461 | 101.2372 | 34 | 5 | 9.315% | 5% | 14.32% | 74.7337 | 74.7337 | 15185.5743 | 2422.1736
3031 | Incheon#1 | Oil | 250 | 115 | 158.3333 | 201.6667 | 245 | 2 | 3 | 6 | 12 | 12999 | 602.9261 | 30.854 | 0.001259 | 1.8232 | 68.4293 | 44 | 4.9 | 12.05% | 4.9% | 16.95% | 74.4107 | 74.4107 | 10264.4007 | 2411.7044
3032 | Incheon#2 | Oil | 250 | 115 | 158.3333 | 201.6667 | 245 | 2 | 3 | 6 | 12 | 13000 | 602.9261 | 30.854 | 0.001259 | 1.8232 | 68.4293 | 44 | 4.9 | 12.05% | 4.9% | 16.95% | 74.4107 | 74.4107 | 10264.4007 | 2411.7044
3033 | Incheon#3 | Oil | 325 | 207 | 240.3333 | 273.6667 | 307 | 2 | 3 | 6 | 12 | 12999 | 828.6445 | 30.854 | 3.6e-05 | 2.3798 | 51.4181 | 16 | 10 | 4.384% | 10% | 14.38% | 78.6677 | 78.6677 | 7712.7092 | 2549.6754
3034 | Incheon#4 | Oil | 325 | 207 | 240.3333 | 273.6667 | 307 | 2 | 3 | 6 | 12 | 13000 | 828.6445 | 30.854 | 3.6e-05 | 2.3798 | 51.4181 | 16 | 10 | 4.384% | 10% | 14.38% | 78.6677 | 78.6677 | 7712.7092 | 2549.6754
4011 | Pyongtack#1 | Oil | 350 | 175 | 230 | 285 | 340 | 5.3 | 5.3 | 6 | 3 | 9897 | 791.2291 | 26.803 | 2e-05 | 2.0037 | 87.4764 | 39 | 5.7 | 10.68% | 5.7% | 16.38% | 60.5923 | 60.5923 | 13121.4541 | 2260.6545
4012 | Pyongtack#2 | Oil | 350 | 175 | 230 | 285 | 340 | 5.3 | 5.3 | 6 | 3 | 9898 | 791.2291 | 26.803 | 2e-05 | 2.0037 | 87.4764 | 39 | 5.7 | 10.68% | 5.7% | 16.38% | 60.5923 | 60.5923 | 13121.4541 | 2260.6545
4013 | Pyongtack#3 | Oil | 350 | 175 | 230 | 285 | 340 | 5.3 | 5.3 | 6 | 3 | 9899 | 791.2291 | 26.803 | 2e-05 | 2.0037 | 87.4764 | 39 | 5.7 | 10.68% | 5.7% | 16.38% | 60.5923 | 60.5923 | 13121.4541 | 2260.6545
4014 | Pyongtack#4 | Oil | 350 | 175 | 230 | 285 | 340 | 5.3 | 5.3 | 6 | 3 | 9900 | 791.2291 | 26.803 | 2e-05 | 2.0037 | 87.4764 | 39 | 5.7 | 10.68% | 5.7% | 16.38% | 60.5923 | 60.5923 | 13121.4541 | 2260.6545
4021 | Ulsan#1 | Oil | 200 | 94 | 129.3333 | 164.6667 | 200 | 2 | 2 | 12 | 22 | 9755 | 485.0554 | 26.346 | 0.000508 | 2.1534 | 34.0652 | 38 | 6.4 | 10.41% | 6.4% | 16.81% | 63.8963 | 63.8963 | 5109.7742 | 2425.2768
4022 | Ulsan#2 | Oil | 200 | 94 | 129.3333 | 164.6667 | 200 | 2 | 2 | 12 | 22 | 9756 | 485.0554 | 26.346 | 0.000508 | 2.1534 | 34.0652 | 38 | 6.4 | 10.41% | 6.4% | 16.81% | 63.8963 | 63.8964 | 5109.7742 | 2425.2768
4023 | Ulsan#3 | Oil | 200 | 94 | 129.3333 | 164.6667 | 200 | 2 | 2 | 12 | 22 | 9757 | 485.0554 | 26.346 | 0.000508 | 2.1534 | 34.0652 | 38 | 6.4 | 10.41% | 6.4% | 16.81% | 63.8963 | 63.8964 | 5109.7742 | 2425.2768
4024 | Ulsan#4 | Oil | 400 | 244 | 289.3333 | 334.6667 | 380 | 8 | 8 | 8 | 12 | 9966 | 919.6663 | 24.845 | 0.000785 | 1.6632 | 128.7803 | 35 | 6.2 | 9.589% | 6.2% | 15.79% | 57.1228 | 57.1228 | 19317.0436 | 2299.1657
4025 | Ulsan#5 | Oil | 400 | 244 | 289.3333 | 334.6667 | 380 | 8 | 8 | 8 | 12 | 9967 | 919.6663 | 24.845 | 0.000785 | 1.6632 | 128.7803 | 35 | 6.2 | 9.589% | 6.2% | 15.79% | 57.1228 | 57.1228 | 19317.0436 | 2299.1657
4026 | Ulsan#6 | Oil | 400 | 244 | 289.3333 | 334.6667 | 380 | 8 | 8 | 8 | 12 | 9968 | 919.6663 | 24.845 | 0.000785 | 1.6632 | 128.7803 | 35 | 6.2 | 9.589% | 6.2% | 15.79% | 57.1228 | 57.1228 | 19317.0436 | 2299.1657
4031 | Yungnam#1 | Oil | 200 | 95 | 126.6667 | 158.3333 | 190 | 4 | 4 | 6 | 22 | 9922 | 482.0446 | 21.973 | 0.000801 | 1.8727 | 75.4568 | 46 | 6.7 | 12.6% | 6.7% | 19.3% | 52.9598 | 52.9598 | 11318.5137 | 2410.2228
4032 | Yungnam#2 | Oil | 200 | 95 | 126.6667 | 158.3333 | 190 | 4 | 4 | 6 | 22 | 9922 | 481.8902 | 21.973 | 0.000791 | 1.8976 | 70.7246 | 46 | 6.7 | 12.6% | 6.7% | 19.3% | 52.9429 | 52.9429 | 10608.6959 | 2409.4512
4041 | Yosu#1 | Oil | 200 | 116 | 142 | 168 | 194 | 2 | 2 | 6 | 12 | 10000 | 474.7104 | 22.603 | 0.002492 | 1.5424 | 66.5496 | 37 | 7 | 10.14% | 7% | 17.14% | 53.6494 | 53.6494 | 9982.4352 | 2373.5518
4042 | Yosu#2 | Oil | 300 | 175 | 214 | 253 | 292 | 3 | 3 | 6 | 12 | 10000 | 761.7901 | 22.603 | 0.000509 | 2.1586 | 68.3953 | 23 | 8.7 | 6.301% | 8.7% | 15% | 57.3958 | 57.3958 | 10259.2896 | 2539.3002
4070 | Ansan | Distributed Gen | 60.8 | 4 | 22 | 40 | 58 | 1.5 | 1.5 | 6 | 6 | 9975 | 185.1838 | 28.647 | 1e-06 | 2.5758 | 28.5687 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 87.2527 | 87.2527 | 4285.2978 | 3045.7869
9191 | Daejon34kongdan | Distributed Gen | 88 | 15 | 37.6667 | 60.3333 | 83 | 5 | 5 | 4 | 4 | 9975 | 227.6992 | 27.45 | 0.001648 | 2.0665 | 33.0826 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 71.0266 | 71.0266 | 4962.3853 | 2587.4913
4091 | Chungju | CC | 61.4 | 9 | 23.3333 | 37.6667 | 52 | 2.7 | 2.7 | 6 | 6 | 9975 | 171.3834 | 28.423 | 1.1e-05 | 2.386 | 24.8403 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 79.336 | 79.336 | 3726.0483 | 2791.2609
4101 | Suwon | CC | 43 | 12 | 20 | 28 | 36 | 1.9 | 1.9 | 6 | 6 | 9975 | 128.7796 | 28.74 | 0.013786 | 1.9155 | 20.9229 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 86.0727 | 86.0727 | 3138.4413 | 2994.875
4111 | Daegu#1 | CC | 44 | 10 | 18 | 26 | 34 | 2 | 2 | 6 | 6 | 9975 | 128.4337 | 28.423 | 0.00585 | 2.287 | 16.4805 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 82.9652 | 82.9652 | 2472.0685 | 2918.9468
4171 | DaesanCC#1 | Distributed Gen | 403 | 110 | 196 | 282 | 368 | 4.5 | 4.5 | 4 | 3 | 9975 | 906.1256 | 29.766 | 1e-06 | 2.1631 | 34.2431 | 41 | 6.5 | 11.23% | 6.5% | 17.73% | 66.9274 | 66.9274 | 5136.4669 | 2248.4505
5011 | Yongdong#1 | Domestic Coal | 125 | 71 | 86.6667 | 102.3333 | 118 | 0.5 | 2 | 7 | 12 | 4540 | 357.4601 | 18.9 | 0.001252 | 2.3314 | 46.4689 | 26 | 6.6 | 7.123% | 6.6% | 13.72% | 54.048 | 54.048 | 6970.3332 | 2859.6811
5012 | Yongdong#2 | Domestic Coal | 200 | 120 | 145 | 170 | 195 | 0.5 | 2 | 8 | 12 | 4540 | 540.9482 | 18.9 | 0.000454 | 2.2534 | 72.1126 | 34 | 7 | 9.315% | 7% | 16.32% | 51.1196 | 51.1196 | 10816.8908 | 2704.741
5031 | Donghae#1 | Domestic Coal | 200 | 125 | 150 | 175 | 200 | 1 | 1 | 10 | 12 | 4687 | 497.3075 | 16.423 | 0.000186 | 2.2381 | 42.2525 | 47 | 5.8 | 12.88% | 5.8% | 18.68% | 40.8364 | 40.8364 | 6337.8682 | 2486.5373
5032 | Donghae#2 | Domestic Coal | 200 | 125 | 150 | 175 | 200 | 1 | 1 | 10 | 12 | 4688 | 497.3075 | 16.423 | 0.000186 | 2.2381 | 42.2525 | 47 | 5.8 | 12.88% | 5.8% | 18.68% | 40.8364 | 40.8364 | 6337.8682 | 2486.5373
5041 | Seocheon#1 | Domestic Coal | 200 | 90 | 123.3333 | 156.6667 | 190 | 2.5 | 2.5 | 7 | 12 | 4631 | 554.3038 | 18.071 | 0.000586 | 2.3928 | 52.3038 | 43 | 6.9 | 11.78% | 6.9% | 18.68% | 50.0841 | 50.0841 | 7845.5656 | 2771.5189
5042 | Seocheon#2 | Domestic Coal | 200 | 90 | 123.3333 | 156.6667 | 190 | 2.5 | 2.5 | 7 | 12 | 4631 | 554.3038 | 18.071 | 0.000586 | 2.3928 | 52.3038 | 43 | 6.9 | 11.78% | 6.9% | 18.68% | 50.0841 | 50.0841 | 7845.5656 | 2771.5189
5051 | Kunsan#1 | Domestic Coal | 66 | 40 | 48.6667 | 57.3333 | 66 | 1 | 1 | 6 | 12 | 4832 | 204.5444 | 22.51 | 0.004541 | 2.3908 | 26.9685 | 23 | 7.1 | 6.301% | 7.1% | 13.4% | 69.762 | 69.762 | 4045.2795 | 3099.1571
6011 | Boryeong#1 | Imported Coal BIT | 500 | 280 | 350 | 420 | 490 | 3 | 5 | 6 | 12 | 6151 | 1153.9773 | 5.487 | 0.000369 | 1.8532 | 135.1333 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.6637 | 12.6637 | 20269.9909 | 2307.9545
6012 | Boryeong#2 | Imported Coal BIT | 500 | 280 | 350 | 420 | 490 | 3 | 5 | 6 | 12 | 6152 | 1153.9773 | 5.487 | 0.000369 | 1.8532 | 135.1333 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.6637 | 12.6637 | 20269.9909 | 2307.9545
6013 | Boryeong#3 | Imported Coal BIT | 500 | 260 | 341 | 422 | 503 | 5 | 8.5 | 6 | 12 | 6151 | 1091.5675 | 5.487 | 0.00029 | 1.8128 | 112.6895 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 11.9789 | 11.9789 | 16903.4284 | 2183.135
6014 | Boryeong#4 | Imported Coal BIT | 500 | 260 | 341 | 422 | 503 | 5 | 8.5 | 6 | 12 | 6152 | 1091.5675 | 5.487 | 0.00029 | 1.8128 | 112.6895 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 11.9789 | 11.9789 | 16903.4284 | 2183.135
6015 | Boryeong#5 | Imported Coal BIT | 500 | 260 | 341 | 422 | 503 | 5 | 8.5 | 6 | 12 | 6153 | 1091.5675 | 5.487 | 0.00029 | 1.8128 | 112.6895 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 11.9789 | 11.9789 | 16903.4284 | 2183.135
6016 | Boryeong#6 | Imported Coal BIT | 500 | 260 | 341 | 422 | 503 | 5 | 8.5 | 6 | 12 | 6154 | 1091.5675 | 5.487 | 0.00029 | 1.8128 | 112.6895 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 11.9789 | 11.9789 | 16903.4284 | 2183.135
6031 | Taean#1 | Imported Coal BIT | 500 | 260 | 341.6667 | 423.3333 | 505 | 10 | 10 | 6 | 12 | 6304 | 1098.1724 | 5.478 | 0.000173 | 1.8779 | 115.9829 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.0316 | 12.0316 | 17397.4344 | 2196.3448
6032 | Taean#2 | Imported Coal BIT | 500 | 260 | 341.6667 | 423.3333 | 505 | 10 | 10 | 6 | 12 | 6305 | 1098.1724 | 5.478 | 0.000173 | 1.8779 | 115.9829 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.0316 | 12.0316 | 17397.4344 | 2196.3448
6033 | Taean#3 | Imported Coal BIT | 500 | 260 | 341.6667 | 423.3333 | 505 | 10 | 10 | 6 | 12 | 6306 | 1098.1724 | 5.478 | 0.000173 | 1.8779 | 115.9829 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.0316 | 12.0316 | 17397.4344 | 2196.3448
6034 | Taean#4 | Imported Coal BIT | 500 | 260 | 341.6667 | 423.3333 | 505 | 10 | 10 | 6 | 12 | 6307 | 1098.1724 | 5.478 | 0.000173 | 1.8779 | 115.9829 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.0316 | 12.0316 | 17397.4344 | 2196.3448
6035 | Taean#5 | Imported Coal BIT | 500 | 260 | 341.6667 | 423.3333 | 505 | 10 | 10 | 6 | 12 | 6304 | 1079.0834 | 5.478 | 0.000176 | 1.8742 | 97.9669 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 11.8224 | 11.8224 | 14695.0317 | 2158.1668
6036 | Taean#6 | Imported Coal BIT | 500 | 260 | 341.6667 | 423.3333 | 505 | 10 | 10 | 6 | 12 | 6305 | 1079.0834 | 5.478 | 0.000176 | 1.8742 | 97.9669 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 11.8224 | 11.8224 | 14695.0317 | 2158.1668
6051 | Hadong#1 | Imported Coal BIT | 500 | 260 | 344.6667 | 429.3333 | 514 | 10 | 10 | 10 | 12 | 6276 | 1087.1941 | 5.546 | 0.000269 | 1.839 | 100.4276 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.0592 | 12.0592 | 15064.1418 | 2174.3882
6052 | Hadong#2 | Imported Coal BIT | 500 | 260 | 344.6667 | 429.3333 | 514 | 10 | 10 | 10 | 12 | 6276 | 1087.1941 | 5.546 | 0.000269 | 1.839 | 100.4276 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.0592 | 12.0592 | 15064.1418 | 2174.3882
6053 | Hadong#3 | Imported Coal BIT | 500 | 260 | 344.6667 | 429.3333 | 514 | 10 | 10 | 10 | 12 | 6276 | 1087.1941 | 5.546 | 0.000269 | 1.839 | 100.4276 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.0592 | 12.0592 | 15064.1418 | 2174.3882
6054 | Hadong#4 | Imported Coal BIT | 500 | 260 | 344.6667 | 429.3333 | 514 | 10 | 10 | 10 | 12 | 6276 | 1087.1941 | 5.546 | 0.000269 | 1.839 | 100.4276 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.0592 | 12.0592 | 15064.1418 | 2174.3882
6055 | Hadong#5 | Imported Coal BIT | 500 | 260 | 344.6667 | 429.3333 | 514 | 10 | 10 | 10 | 12 | 6276 | 1087.1941 | 5.546 | 0.000269 | 1.839 | 100.4276 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.0592 | 12.0592 | 15064.1418 | 2174.3882
6056 | Hadong#6 | Imported Coal BIT | 500 | 260 | 344.6667 | 429.3333 | 514 | 10 | 10 | 10 | 12 | 6276 | 1087.1941 | 5.546 | 0.000269 | 1.839 | 100.4276 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.0592 | 12.0592 | 15064.1418 | 2174.3882
6071 | Samchonpo#1 | Imported Coal BIT | 560 | 280 | 366.6667 | 453.3333 | 540 | 5 | 5 | 9 | 12 | 6037 | 1291.4561 | 5.494 | 0.000754 | 1.4963 | 217.0928 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.6701 | 12.6701 | 32563.9139 | 2306.1716
6072 | Samchonpo#2 | Imported Coal BIT | 560 | 280 | 366.6667 | 453.3333 | 540 | 5 | 5 | 9 | 12 | 6037 | 1291.4561 | 5.494 | 0.000754 | 1.4963 | 217.0928 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.6701 | 12.6701 | 32563.9139 | 2306.1716
6073 | Samchonpo#3 | Imported Coal BIT | 560 | 280 | 370 | 460 | 550 | 6 | 6 | 9 | 12 | 6156 | 1295.4851 | 5.494 | 0.001138 | 1.1778 | 279.028 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.7096 | 12.7096 | 41854.1964 | 2313.3662
6074 | Samchonpo#4 | Imported Coal BIT | 560 | 280 | 370 | 460 | 550 | 6 | 6 | 9 | 12 | 6156 | 1295.4851 | 5.494 | 0.001138 | 1.1778 | 279.028 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 12.7096 | 12.7096 | 41854.1964 | 2313.3662
6075 | Samchonpo#5 | Imported Coal BIT | 500 | 260 | 338 | 416 | 494 | 3 | 3 | 9 | 12 | 6156 | 1083.8656 | 5.494 | 0.00029 | 1.8106 | 106.0476 | 38 | 5 | 10.41% | 5% | 15.41% | 11.9095 | 11.9095 | 15907.1333 | 2167.7311
6076 | Samchonpo#6 | Imported Coal BIT | 500 | 260 | 338 | 416 | 494 | 3 | 3 | 9 | 12 | 6156 | 1083.8656 | 5.494 | 0.00029 | 1.8106 | 106.0476 | 38 | 5 | 10.41% | 5% | 15.41% | 11.9095 | 11.9095 | 15907.1333 | 2167.7311
6091 | Dangjin#1 | Imported Coal BIT | 500 | 260 | 350 | 440 | 530 | 10 | 10 | 6 | 12 | 6169 | 1096.9925 | 5.466 | 6.9e-05 | 1.9688 | 95.3345 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 11.9923 | 11.9923 | 14300.1767 | 2193.985
6092 | Dangjin#2 | Imported Coal BIT | 500 | 260 | 350 | 440 | 530 | 10 | 10 | 6 | 12 | 6170 | 1096.9925 | 5.466 | 6.9e-05 | 1.9688 | 95.3345 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 11.9923 | 11.9923 | 14300.1767 | 2193.985
6093 | Dangjin#3 | Imported Coal BIT | 500 | 260 | 350 | 440 | 530 | 10 | 10 | 6 | 12 | 6171 | 1096.9925 | 5.466 | 6.9e-05 | 1.9688 | 95.3345 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 11.9923 | 11.9923 | 14300.1767 | 2193.985
6094 | Dangjin#4 | Imported Coal BIT | 500 | 260 | 350 | 440 | 530 | 10 | 10 | 6 | 12 | 6172 | 1096.9925 | 5.466 | 6.9e-05 | 1.9688 | 95.3345 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 11.9923 | 11.9923 | 14300.1767 | 2193.985
6111 | Honam#1 | Imported Coal BIT | 250 | 120 | 163.3333 | 206.6667 | 250 | 3 | 3 | 6 | 12 | 5749 | 646.7792 | 7.308 | 6e-06 | 2.439 | 36.643 | 67 | 7.9 | 18.36% | 7.9% | 26.26% | 18.9066 | 18.9067 | 5496.4437 | 2587.1168
6112 | Honam#2 | Imported Coal BIT | 250 | 120 | 163.3333 | 206.6667 | 250 | 3 | 3 | 6 | 12 | 5750 | 646.7792 | 7.308 | 6e-06 | 2.439 | 36.643 | 67 | 7.9 | 18.36% | 7.9% | 26.26% | 18.9066 | 18.9067 | 5496.4437 | 2587.1168
7011 | Kori#1 | Nuclear | 587 | 360 | 435 | 510 | 585 | 0.3 | 0.3 | 8 | 12 | 2500 | 1491.0584 | 1.407 | 5e-05 | 2.2103 | 176.3604 | 46 | 5.8 | 12.6% | 5.8% | 18.4% | 3.574 | 3.574 | 26454.0564 | 2540.1336
7012 | Kori#2 | Nuclear | 650 | 415 | 492.3333 | 569.6667 | 647 | 0.3 | 0.3 | 8 | 12 | 2500 | 1652.4773 | 1.624 | 0.000173 | 2.0249 | 263.1836 | 46 | 5.8 | 12.6% | 5.8% | 18.4% | 4.1287 | 4.1287 | 39477.5325 | 2542.2728
7013 | Kori#3 | Nuclear | 950 | 795 | 860 | 925 | 990 | 0.6 | 0.6 | 22 | 8 | 2500 | 2367.4764 | 1.43 | 1.7e-05 | 2.3505 | 119.2007 | 38 | 5.6 | 10.41% | 5.6% | 16.01% | 3.5637 | 3.5637 | 17880.1087 | 2492.0804
7014 | Kori#4 | Nuclear | 950 | 795 | 858.3333 | 921.6667 | 985 | 0.6 | 0.6 | 22 | 8 | 2500 | 2362.9421 | 1.487 | 1.7e-05 | 2.3457 | 119.2007 | 38 | 5.6 | 10.41% | 5.6% | 16.01% | 3.6986 | 3.6986 | 17880.1087 | 2487.3074
7031 | Wolsong#1 | Nuclear | 678.683 | 577 | 609.6667 | 642.3333 | 675 | 2.3 | 3.4 | 8 | 8 | 2500 | 1857.8564 | 0.789 | 0.000238 | 2.0017 | 389.7357 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 2.1598 | 2.1598 | 58460.3598 | 2737.4435
7032 | Wolsong#2 | Nuclear | 700 | 614 | 650 | 686 | 722 | 2.4 | 3.6 | 8 | 8 | 2500 | 1899.0778 | 0.917 | 0.000236 | 1.991 | 389.7357 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 2.4878 | 2.4878 | 58460.3598 | 2712.9683
7033 | Wolsong#3 | Nuclear | 700 | 611 | 647 | 683 | 719 | 2.4 | 3.6 | 8 | 8 | 2500 | 1922.3892 | 0.873 | 0.000243 | 2.0194 | 389.7357 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 2.3975 | 2.3975 | 58460.3598 | 2746.2703
7034 | Wolsong#4 | Nuclear | 700 | 611 | 647 | 683 | 719 | 2.4 | 3.6 | 8 | 8 | 2500 | 1922.3892 | 0.902 | 0.000243 | 2.0194 | 389.7357 | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 2.4771 | 2.4771 | 58460.3598 | 2746.2703
7051 | Yonggwang#1 | Nuclear | 950 | 758 | 826.6667 | 895.3333 | 964 | 0.8 | 0.8 | 21 | 9 | 2500 | 2333.6912 | 1.529 | 0.000144 | 2.0294 | 275.7832 | 40 | 5.6 | 10.96% | 5.6% | 16.56% | 3.756 | 3.756 | 41367.4745 | 2456.5171
7052 | Yonggwang#2 | Nuclear | 950 | 755 | 824.3333 | 893.6667 | 963 | 0.8 | 0.8 | 21 | 9 | 2500 | 2359.6718 | 1.426 | 0.000148 | 2.053 | 275.7832 | 40 | 5.6 | 10.96% | 5.6% | 16.56% | 3.542 | 3.542 | 41367.4745 | 2483.8651
7053 | Yonggwang#3 | Nuclear | 1000 | 750 | 836.6667 | 923.3333 | 1010 | 0.6 | 0.9 | 10 | 10 | 2500 | 2404.1608 | 1.512 | 0.000251 | 2.0563 | 96.8778 | 45 | 4.9 | 12.33% | 4.9% | 17.23% | 3.6351 | 3.6351 | 14531.6718 | 2404.1608
7054 | Yonggwang#4 | Nuclear | 1000 | 750 | 836.6667 | 923.3333 | 1010 | 0.6 | 0.9 | 10 | 10 | 2500 | 2424.7438 | 1.409 | 0.000255 | 2.0729 | 96.8778 | 45 | 4.9 | 12.33% | 4.9% | 17.23% | 3.4165 | 3.4165 | 14531.6718 | 2424.7438
7055 | Yonggwang#5 | Nuclear | 1000 | 713 | 812 | 911 | 1010 | 0.6 | 0.6 | 8 | 12 | 2500 | 2406.4978 | 1.37 | 0.000525 | 1.2132 | 668.2478 | 45 | 4.9 | 12.33% | 4.9% | 17.23% | 3.2969 | 3.2969 | 100237.1763 | 2406.4978
7056 | Yonggwang#6 | Nuclear | 1000 | 720 | 816 | 912 | 1008 | 0.6 | 0.6 | 8 | 12 | 2500 | 2406.4978 | 1.466 | 0.000525 | 1.2132 | 668.2478 | 45 | 4.9 | 12.33% | 4.9% | 17.23% | 3.5279 | 3.5279 | 100237.1763 | 2406.4978
7071 | Ulchin#1 | Nuclear | 950 | 784 | 841 | 898 | 955 | 0.5 | 0.5 | 8 | 8 | 2500 | 2378.0139 | 1.368 | 0.000188 | 1.9575 | 348.6742 | 37 | 5.6 | 10.14% | 5.6% | 15.74% | 3.4243 | 3.4243 | 52301.1301 | 2503.1725
7072 | Ulchin#2 | Nuclear | 950 | 784 | 840 | 896 | 952 | 0.5 | 0.5 | 8 | 8 | 2500 | 2375.1477 | 1.432 | 0.000187 | 1.9555 | 348.6742 | 37 | 5.6 | 10.14% | 5.6% | 15.74% | 3.5802 | 3.5802 | 52301.1301 | 2500.1555
7073 | Ulchin#3 | Nuclear | 1000 | 795 | 866.6667 | 938.3333 | 1010 | 0.6 | 0.6 | 8 | 10 | 2500 | 2539.5332 | 1.478 | 0.000195 | 1.9959 | 348.6742 | 48 | 4.9 | 13.15% | 4.9% | 18.05% | 3.7534 | 3.7534 | 52301.1301 | 2539.5332
7074 | Ulchin#4 | Nuclear | 1000 | 795 | 865 | 935 | 1005 | 0.6 | 0.6 | 8 | 10 | 2500 | 2510.5832 | 1.486 | 0.00019 | 1.9719 | 348.6742 | 48 | 4.9 | 13.15% | 4.9% | 18.05% | 3.7307 | 3.7307 | 52301.1301 | 2510.5832
| New Nuclear | [12 empty] | 1.466 |  |  |  | 45 | 4.9 | 12.33% | 4.9% | 17.23% | 3.3938 | 3.3938 |  | 2315
| New Coal | [12 empty] | 5.478 |  |  |  | 38 | 4.9 | 10.41% | 4.9% | 15.31% | 11.4545 | 11.4545 |  | 2091
| New D_Coal | [12 empty] | 16.423 |  |  |  | 43 | 7.9 | 11.78% | 7.9% | 19.68% | 37.2802 | 37.2802 |  | 2270
| New Oil | [12 empty] | 20.91 |  |  |  | 38 | 5.1 | 10.41% | 5.1% | 15.51% | 43.7228 | 43.7228 |  | 2091
| New CC | [12 empty] | 33.292 |  |  |  | 41 | 7.2 | 11.23% | 7.2% | 18.43% | 55.4978 | 55.4978 |  | 1667
8103 | Namjeju | Jeju Island - Oil | 20 | 5 | 9.6667 | 14.3333 | 19 | 0.2 | 0.1 | 12 | 10 | 9954 | 63.936 | 26.207 | 0.004153 | 3.0067 | 2.1402 | 26 | 2.5 | 7.123% | 2.5% | 9.623% | 83.7785 | 83.7785 | 321.0335 | 3196.7982
8111 | Jejumosun | Jeju Island - Oil | 10 | 5 | 6.6667 | 8.3333 | 10 | 0.1 | 0.1 | 6 | 12 | 9998 | 33.1744 | 26.5 | 0.06203 | 2.1 | 5.9713 | 26 | 2.5 | 7.123% | 2.5% | 9.623% | 87.9122 | 87.9122 | 895.6883 | 3317.4425
8112 | Jeju#2 | Jeju Island - Oil | 75 | 42 | 53 | 64 | 75 | 1 | 1 | 6 | 12 | 9934 | 181.9666 | 26.423 | 0.002545 | 1.8323 | 30.2307 | 26 | 2.5 | 7.123% | 2.5% | 9.623% | 64.1081 | 64.1081 | 4534.6113 | 2426.2216
8113 | Jeju#3 | Jeju Island - Oil | 75 | 42 | 53 | 64 | 75 | 1 | 1 | 6 | 12 | 9934 | 179.8992 | 26.423 | 0.00094 | 2.0161 | 23.4013 | 26 | 2.5 | 7.123% | 2.5% | 9.623% | 63.3797 | 63.3797 | 3510.1988 | 2398.6557
8321 | HanlimCC#1 | Jeju Island - CC | 105 | 41 | 63.6667 | 86.3333 | 109 | 8.8 | 8.8 | 4 | 3 | 8953 | 221.4159 | 47.195 | 1.1e-05 | 1.9476 | 16.8004 | 34 | 6.5 | 9.315% | 6.5% | 15.82% | 99.5212 | 99.5212 | 2520.0591 | 2108.7228
8513 | JejuGT#3 | Jeju Island - GT | 55 | 15 | 27 | 39 | 51 | 5 | 5 | 1 | 1 | 8954 | 160.8854 | 49.452 | 6.3e-05 | 1.9439 | 53.7797 | 26 | 4 | 7.123% | 4% | 11.12% | 144.6564 | 144.6564 | 8066.9621 | 2925.1886
8615 | Namjeju#1 | Jeju Island - Diesel Engeine | 20 | 7 | 11 | 15 | 19 | 0.3 | 0.5 | 4 | 1 | 9954 | 43.5532 | 26.207 | 0.005524 | 1.9992 | 1.3598 | 26 | 4 | 7.123% | 4% | 11.12% | 57.0699 | 57.07 | 203.965 | 2177.6604
8616 | Namjeju#2 | Jeju Island - Diesel Engeine | 20 | 7 | 11 | 15 | 19 | 0.3 | 0.5 | 4 | 1 | 9954 | 43.5532 | 26.207 | 0.005524 | 1.9992 | 1.3598 | 26 | 4 | 7.123% | 4% | 11.12% | 57.0699 | 57.07 | 203.965 | 2177.6604

## Heat Rate Curve
|  |  | Num | 74
kCal = Constant + Slope x kW + Square x (kW)^2
Plant |  | Constant | Slope | Square
Yosu#2 | Oil | 68.3953 | 2.1586 | 0.000509 | Capacity | 300
Increment | Capacity - kW | Energy -kCal | Avg HR - kCal/kWh | Incremental Heat Rate
10% | 30 | 133.6118 | 4453.7281
20% | 60 | 199.7446 | 3329.0771 | 2204.426
30% | 90 | 266.7936 | 2964.3734 | 2234.966
40% | 120 | 334.7588 | 2789.6565 | 2265.506
50% | 150 | 403.6402 | 2690.9344 | 2296.046
60% | 180 | 473.4377 | 2630.2097 | 2326.586
70% | 210 | 544.1515 | 2591.1977 | 2357.126
80% | 240 | 615.7815 | 2565.7563 | 2387.666
90% | 270 | 688.3277 | 2549.3618 | 2418.206
100% | 300 | 761.7901 | 2539.3002 | 2448.746
Yosu#2 Oil

## Names
Code | Name
1010 | 화천 | Hwacheon
1020 | 춘천 | Chuncheon
1030 | 의암 | Uiam
1040 | 청평 | Cheongpyong
1050 | 팔당 | Paldang
1060 | 강릉 | kanglung
1070 | 소양강 | Soyangkang
1080 | 충주 | Choongju
1090 | 대청 | Daecheong
1100 | 안동 | Andong
1110 | 합천 | Habcheon
1120 | 임하 | Imha
1140 | 섬진강수력 | Sumjinkang
9990 | 구입전력 | PurchargedPower
1170 | 주암수력 | Juam
1190 | 용담수력#1 | Yongdam#1
1610 | 무주양수 | MujuPS
1620 | 삼랑진양수 | SamlangjinPS
1630 | 청평양수 | CheongpyongPS
1650 | 산청양수 | SancheongPS
2021 | 서인천복합1GT#1 | Seoincheon1GT#1
2022 | 서인천복합1GT#2 | Seoincheon1GT#2
2023 | 서인천복합1GT#3 | Seoincheon1GT#3
2024 | 서인천복합1GT#4 | Seoincheon1GT#4
2031 | 서인천복합1CC#1 | Seoincheon1CC#1
2032 | 서인천복합1CC#2 | Seoincheon1CC#2
2033 | 서인천복합1CC#3 | Seoincheon1CC#3
2034 | 서인천복합1CC#4 | Seoincheon1CC#4
2051 | 서인천복합1GT#5 | Seoincheon1GT#5
2052 | 서인천복합1GT#6 | Seoincheon1GT#6
2053 | 서인천복합1GT#7 | Seoincheon1GT#7
2054 | 서인천복합1GT#8 | Seoincheon1GT#8
2061 | 서인천복합1CC#5 | Seoincheon1CC#5
2062 | 서인천복합1CC#6 | Seoincheon1CC#6
2063 | 서인천복합1CC#7 | Seoincheon1CC#7
2064 | 서인천복합1CC#8 | Seoincheon1CC#8
2073 | 신인천복합2GT1 | Shinincheon2GT1
2074 | 신인천복합2GT2 | Shinincheon2GT2
2091 | 신인천복합2CC#9 | Shinincheon2CC#9
2092 | 신인천복합2CC#10 | Shinincheon2CC#10
2103 | 신인천복합2GT3 | Shinincheon2GT3
2104 | 신인천복합2GT4 | Shinincheon2GT4
2121 | 신인천복합2CC#11 | Shinincheon2CC#11
2122 | 신인천복합2CC#12 | Shinincheon2CC#12
2191 | 안양복합GT1 | AnyangGT1
2211 | 안양복합CC#1 | AnyangCC#1
2243 | 분당복합GT1 | BundangGT1
2244 | 분당복합GT2 | BundangGT2
2271 | 분당복합CC#1 | BundangCC#1
2272 | 분당복합CC#2 | BundangCC#2
2283 | 일산복합GT1 | IlsanGT1
2284 | 일산복합GT2 | IlsanGT2
2311 | 일산복합CC#1 | IlsanCC#1
2312 | 일산복합CC#2 | IlsanCC#2
2321 | 부천복합GT1 | BucheonGT1
2341 | 부천복합CC#1 | BucheonCC#1
2351 | 평택복합GT1 | PyongtackGT1
2381 | 평택복합CC#1 | PyongtackCC#1
2393 | 울산복합GT1 | UlsanGT1
2394 | 울산복합GT2 | UlsanGT2
2395 | 울산복합GT3 | UlsanGT3
2431 | 울산복합CC#1 | UlsanCC#1
2432 | 울산복합CC#2 | UlsanCC#2
2433 | 울산복합CC#3 | UlsanCC#3
2443 | 보령복합GT1 | BoryeongGT1
2444 | 보령복합GT2 | BoryeongGT2
2445 | 보령복합GT3 | BoryeongGT3
2446 | 보령복합GT4 | BoryeongGT4
2481 | 보령복합CC#1 | BoryeongCC#1
2482 | 보령복합CC#2 | BoryeongCC#2
2483 | 보령복합CC#3 | BoryeongCC#3
2484 | 보령복합CC#4 | BoryeongCC#4
2503 | 한화복합GT1 | HanhwaGT1
2504 | 한화복합GT2 | HanhwaGT2
2505 | 한화복합GT3 | HanhwaGT3
2506 | 한화복합GT4 | HanhwaGT4
2551 | 한화복합CC#1 | HanhwaCC#1
2552 | 한화복합CC#2 | HanhwaCC#2
2553 | 한화복합CC#3 | HanhwaCC#3
2554 | 한화복합CC#4 | HanhwaCC#4
2561 | 부곡복합GT1 | BugokGT1
2581 | 부곡복합CC#1 | BugokCC#1
2591 | 목동열병합#1 | Mokdong#1
2601 | 노원열병합#1 | Nowon#1
2611 | 부산복합GT1 | PusanGT1
2612 | 부산복합GT2 | PusanGT2
2631 | 부산복합CC1 | PusanCC1
2632 | 부산복합CC2 | PusanCC2
3014 | 서울#4 | Seoul#4
3015 | 서울#5 | Seoul#5
3031 | 인천#1 | Incheon#1
3032 | 인천#2 | Incheon#2
3033 | 인천#3 | Incheon#3
3034 | 인천#4 | Incheon#4
4011 | 평택#1 | Pyongtack#1
4012 | 평택#2 | Pyongtack#2
4013 | 평택#3 | Pyongtack#3
4014 | 평택#4 | Pyongtack#4
4021 | 울산#1 | Ulsan#1
4022 | 울산#2 | Ulsan#2
4023 | 울산#3 | Ulsan#3
4024 | 울산#4 | Ulsan#4
4025 | 울산#5 | Ulsan#5
4026 | 울산#6 | Ulsan#6
4031 | 영남#1 | Yungnam#1
4032 | 영남#2 | Yungnam#2
4041 | 여수#1 | Yosu#1
4042 | 여수#2 | Yosu#2
4070 | 안산도시개발 | Ansan
9191 | 대전3,4공단 | Daejon34kongdan
4091 | 청주열병합 | Chungju
4101 | 수원열병합#1 | Suwon
4111 | 대구열병합#1 | Daegu#1
4151 | 대산복합GT1 | DaesanGT1
4152 | 대산복합GT2 | DaesanGT2
4171 | 대산복합CC#1 | DaesanCC#1
5011 | 영동#1 | Yongdong#1
5012 | 영동#2 | Yongdong#2
5031 | 동해#1 | Donghae#1
5032 | 동해#2 | Donghae#2
5041 | 서천#1 | Seocheon#1
5042 | 서천#2 | Seocheon#2
5051 | 군산#1 | Kunsan#1
6011 | 보령#1 | Boryeong#1
6012 | 보령#2 | Boryeong#2
6013 | 보령#3 | Boryeong#3
6014 | 보령#4 | Boryeong#4
6015 | 보령#5 | Boryeong#5
6016 | 보령#6 | Boryeong#6
6031 | 태안#1 | Taean#1
6032 | 태안#2 | Taean#2
6033 | 태안#3 | Taean#3
6034 | 태안#4 | Taean#4
6035 | 태안#5 | Taean#5
6036 | 태안#6 | Taean#6
6051 | 하동#1 | Hadong#1
6052 | 하동#2 | Hadong#2
6053 | 하동#3 | Hadong#3
6054 | 하동#4 | Hadong#4
6055 | 하동#5 | Hadong#5
6056 | 하동#6 | Hadong#6
6071 | 삼천포#1 | Samchonpo#1
6072 | 삼천포#2 | Samchonpo#2
6073 | 삼천포#3 | Samchonpo#3
6074 | 삼천포#4 | Samchonpo#4
6075 | 삼천포#5 | Samchonpo#5
6076 | 삼천포#6 | Samchonpo#6
6091 | 당진#1 | Dangjin#1
6092 | 당진#2 | Dangjin#2
6093 | 당진#3 | Dangjin#3
6094 | 당진#4 | Dangjin#4
6111 | 호남#1 | Honam#1
6112 | 호남#2 | Honam#2
7011 | 고리#1 | Kori#1
7012 | 고리#2 | Kori#2
7013 | 고리#3 | Kori#3
7014 | 고리#4 | Kori#4
7031 | 월성#1 | Wolsong#1
7032 | 월성#2 | Wolsong#2
7033 | 월성#3 | Wolsong#3
7034 | 월성#4 | Wolsong#4
7051 | 영광#1 | Yonggwang#1
7052 | 영광#2 | Yonggwang#2
7053 | 영광#3 | Yonggwang#3
7054 | 영광#4 | Yonggwang#4
7055 | 영광#5 | Yonggwang#5
7056 | 영광#6 | Yonggwang#6
7071 | 울진#1 | Ulchin#1
7072 | 울진#2 | Ulchin#2
7073 | 울진#3 | Ulchin#3
7074 | 울진#4 | Ulchin#4
8103 | 남제주기력 | Namjeju
8111 | 제주모선기력 | Jejumosun
8112 | 제주기력#2 | Jeju#2
8113 | 제주기력#3 | Jeju#3
8301 | 한림GT#1 | HanlimGT#1
8321 | 한림CC#1 | HanlimCC#1
8513 | 제주GT#3 | JejuGT#3
8615 | 남제주내연#1 | Namjeju#1
8616 | 남제주내연#2 | Namjeju#2
8630 | 제주모선내연 | Jejumosunnaeyon
9991 | 비중앙급전 | Nondispatch

## New Plant_EFOR&MOR&Heat Rate
I/O Curve Formula "Y = a + a1*X + a2*X^2"
Formula Calculating Heat Rate with I/O Curve "H/R=Y÷X1 = (a + a1*X1 + a2*X1^2)÷X1" , when X1 is Output.
Criteria of dividing Block
Type | First Block's H/R | Second Block's H/R | Third Block's H/R
Nuclear | 90% | - | 100%
Steam | 50% | 75% | 100%
CC | Existing : 33% | 75% | 100%
New : 30%
Projected Data for New Generation Plant
Type | Capacity | MOR | EFOR | Heat Rate
|  |  |  | First Block |  | Second Block |  |  | Third Block |  | Average Incremental Heat Rate
|  |  |  | MW | H/R | MW | H/R | H/R | MW | H/R
Nuclear | 1000 MW | 44 | 4.9 | 900 | 2338 | - | - | - | 1000 | 2315 | 2018
(PWR) | 1400 MW | 51 | 4.9 | 1260 | 2433 | - | - | - | 1400 | 2364 | 2193
Coal | 500 MW | 38 | 4.9 | 250 | 2179 | 375 | 2112 | 2112 | 500 | 2091 | 2003
| 800 MW | 43 | 4.9 | 400 | 2036 | 600 | 1991 | 1991 | 800 | 1977 | 1918
D_Coal | 200 MW | 37 | 5.8 | 100 | 2427 | 150 | 2308 | 2308 | 200 | 2270 | 2113
Oil | 500 MW | 38 | 4.9 | 250 | 2179 | 375 | 2112 | 2112 | 500 | 2091 | 2003
CC | 450 MW | 41 | 6.5 | 135 | 1944 | 338 | 1706 | 1706 | 450 | 1667 | 1548
Pumped | 300 MW | 41 | 1.5 | - | - | - |  | - | - | - | -
`