## Slide 1: Mini-grid Corporate Model

## Slide 2: Introduction
Mini-grid is a corporate model
  Carefully modelling a mini-grid provides the basis for other issues
  Think about EDF providing power to the city of Paris or the country of France
  Think about a data centre powered with solar and battery or nuclear
  Think about powering an electrolyzer with alternative strategies
Why a mini-grid model is corporate model and not a project finance model
  The model must consider both supply and demand, project finance is only supply
  Portfolio of assets with different lives, not one asset with a limited life
  The mini-grid does not end; there will be come kind of terminal value or liability
  Capital expenditures to replace and augment

## Slide 3: History of Model Development
Reviewed models for other countries
Created model framework using PVGIS hourly data
Constructed model framework for different clients
Observed models that are project finance based and too simplistic
Reviewed and evaluated quality data from Mozambique

## Slide 4: Other Models Reviewed
Model from Nigeria
Model from Tunesia
Other Financial Models (World Bank)
Earlier Models Created
Use of other mini-grid model as a starting point
  Nigeria case
  Uses InputC and InputS with financial model
  No supply and demand
  No degradation or augmentation
  No terminal value
Problems with other mini-grid models
  The big variable is how much diesel must be used – no ability to measure this
  No ability to evaluate the cost of mini-grid with different load profiles
  Cannot measure the effect of unserved energy
  Does not measure the effect of incorrectly sizing solar and battery for the system

## Slide 5: Examples of Other Models – Too Simple to Model the Essence of Case Studies
What is not in the inputs
  Nothing about load shapes
  Degradation is not used
  No capital cost of solar and batteries
  Nothing about solar production for batteries, state of charge, round trip efficiency
  Nothing about diesel requirement, diesel price, diesel heat rate
  Nothing about capital cost of replacement

## Slide 6: Simple Model Output
No replacement capital expenditures
No evaluation of diesel cost from load shape
No quantification of over-size or under-size the mini-grid
No augmentation for the growth
No detail of distribution and generation costs

## Slide 7: Data Sources and Model Data

## Slide 8: Sources of Data
Actual Systems
  High quality data for operations
  Data on growth in demand
Cost Data from
Data from Tariff Setting
Current Data on Solar Costs and Battery Systems from China

## Slide 9: Method for Evaluating GCF Funding
Use actual case studies with load shapes, load growth, tariffs, minimum state of charge, diesel prices, distribution costs.
Framework for evaluating added funding requirement
Create downside and upside cases
  Alternative growth scenarios
  Alternative losses
  Alternative replacement cost equations and assumptions
  Alternative solar production from drivers of performance ratio
  Alternative battery characteristics (round trip efficiency, degradation, minimum state of charge)

## Slide 10: Case Studies

## Slide 11: Use of Case Studies for Analysis
Case Studies of existing projects implemented by that contain high quality data for:
  Load growth
  Operation of solar relative to irradiation allowing analysis of performance ratio
  Operation of battery including state of charge, round trip efficiency and degradation
  Distribution characteristics allowing cost analysis
Case studies have different characteristics that can be used to evaluate required funding from the GFC including.
  Different Load Shapes
  Different Size and ramp-up rates
  Different Load Growth
  Different Solar Irradiation
  Different Capacity Structure (Solar relative to Battery and Diesel)
Different case studies with alternative load, size, distribution allow for analysis of characteristics and the effect on required support

## Slide 12: Operational Inputs for Case 1 - Nagonha Mini Grid

## Slide 13: Case 1 Mini Grid

## Slide 14: Energy Consumption
Use this to establish the base case annual demand. We make alternative load growth assumptions going forward. Annualizing the last four months produces a base value of 252,153 kWh per year.

## Slide 15: Illustration of Inputs for Capacity and Deman Growth
First part of inputs has sizing of capacity and annual demand.
Use the notion of constant inputs and time series that is now common in models.
Use the drop-down box to simulate different cases.

## Slide 16: Case 1 – Mini Grid Load Curves
The fact that hourly loads are provided allows dispatch analysis in the financial model when combined with solar and battery. For this system, note that the load increases after sundown. Similar usage pattern in 2025; but increase from load growth. The load from 2025 is used as a baseline.
Note in the right-hand graph that the increase in load happens slightly later because of the timing of the sundown.

## Slide 17: More Load Curves
.

## Slide 18: Hourly Demand Patterns per Month
Different hourly demands are entered by month in the model
Hourly demands are resolved to annual demands using the resolve button
Simulation of hourly solar, battery charge and discharge and remaining diesel using the Simulate Demand and Supply button

## Slide 19: Demand and Supply in Financial Model
Illustration of demand and supply

## Slide 20: Solar Irradiation - Actual
Solar irradiation is provided for Nagonha. We have used the latitude and longitude to evaluate the hourly irradiation from the EU website that provides hourly irradiation.

## Slide 21: Comparison of Hourly Irradiation with PVGIS Hourly Irradiation
The hourly irradiation produced by PVGIS produces values from 2005 to 2023 which does not cover the actual period. But comparison can be used to evaluate the general levels of solar and the patterns. The google earth shows the latitude and longitude. The

## Slide 22: Simulated Solar Irradiation from PVGIS
Download the hourly solar irradiation for each system.
Use fixed tilt system
Observe the different patterns in different seasons

## Slide 23: Hourly Solar Production and Performance Ratio
Will correlate this with PVGIS to derive the performance ratio. Note that there was too much solar in the early period relative to the battery, but this was resolved with the increase in load. Note that in July 2024, there is too much solar relative to the battery but in December, all of the solar is used to charge the battery.
The level of solar production in February 2025 can be used to gauge an approximate performance ratio during the peak hours. Production is about 165 kW, and the capacity of the solar project is 200 kWp. This implies a performance ratio of 82.5% during the peak hours.

## Slide 24: Battery Usage
Note the change in the battery usage over time. As load grows the battery state of charge declines and becomes near 15%. We assume a minimum state of charge of 15% as described in the next slide.

## Slide 25: Inputs for Battery, Solar and Diesel Characteristics
Can change the assumptions and evaluate the effect on diesel production.

## Slide 26: Simulation of Solar, Battery and Diesel – One Week Example
Simulation for one week
Note that when the solar is less, the diesel is more.
Driven by battery capacity, round trip efficiency and state of charge.

## Slide 27: Simulation of Battery and Diesel for One Day
Note that not enough batter plus solar to meet the demand

## Slide 28: Temperature and Electricity Usage for Battery
.

## Slide 29: Battery State of Charge of 15% and Start of Diesel
.
Note the diesel efficiency of 40% above. Below 77.7 Liters/311 kWh implies a heat rate of .25 which is extremely good. The heat rate is an input to the model.

## Slide 30: Simulation of Diesel Replacement from Hours Run
.

## Slide 31: Revenue Summary
The revenue summary is presented. Not the average price of 8.44 which converts to .
Note the comment about the initial sales which is why the energy sales are high at the beginning of the mini-grid and then go down.

## Slide 32: Results of Base Cases
Base Case and Downside Case

## Slide 33: Case 2

## Slide 34: Mini-grid Capacity and Customers
This is the largest system in terms of number of customers

## Slide 35: Issues
Why does the performance ratio seem to be so low
Effect of the load curve that has much less usage during sunlight hours
Larger system with less penetration

## Slide 36: Daily Consumption and Annual Demand

## Slide 37: Cost Structure and Loads in Case 1 vs Case 2
Evaluate the dramatic difference in loads

## Slide 38: Location of Mini-Grid for PVGIS
.

## Slide 39: PVGIS for Mini-Grid
.

## Slide 40: Idugo Solar Irradiation – November 2024
.

## Slide 41: Idugo Irradiation – March 2025
.

## Slide 42: Idugo Irradiation February 2025

## Slide 43: Peak Solar Production and Implied PR
The peak production should occur when the solar irradiation is about 1,000 kWh/m2. The level of 140 kW relative to the size of the plant at 231 kWp implies a performance ratio for the peak hour of only 60%. This is much lower than the 75% shown in the earlier slide.

## Slide 44: Hourly Solar Production and Battery Constraint
The hourly solar production demonstrates that solar may be wasted.

## Slide 45: Battery is Over-sized for Current Demand
Note how the state of charge does not reach the minimum state of charge except on a few occasions.

## Slide 46: Depth of Discharge and Battery Discussion for Idugo
.

## Slide 47: Idugo Battery Temperature
They even present the battery temperature

## Slide 48: Idugo Tariff
Note that the rate is the same for each system. An issue for modelling is the assumption of rate increases over time.

## Slide 49: Base Case with 80% Grant
.

## Slide 50: Case 3

## Slide 51: Smaller System with Less Load Relative to Supply

## Slide 52: Issues Raised in Mugulama Case
Change in Load Profile
Data on the Temperature on the Panel
Very small system, but more load than Muite

## Slide 53: Mugulama - Electricity Demand
The average daily demand is around 200 kWh per day. 200 kWh x 365 = 73,000 kWh per year.

## Slide 54: Case 3 Load Curve
.

## Slide 55: Case 3 Annual and Daily Demand
Title of graph is wrong. Assume 14 kWh per day.
,

## Slide 56: Irradiation Benchmark and Panel Temperature
Note how the temperature on the PV panel reaches a lot more than 60 degrees. This is discussed in the Appendix.

## Slide 57: Location of Mini-Grid for PVGIS
Location and Longitude and Latitude

## Slide 58: Solar Irradiation from PVGIS
PVGIS

## Slide 59: Hourly Production
Solar Production of about 55 kW relative to the capacity of 76 kWp. Implies a performance ratio of 72%.

## Slide 60: Peak Power Production – 76 kWp
.

## Slide 61: Base Case
.

## Slide 62: Case 4 – Mini-grid

## Slide 63: Muite Mini-grid

## Slide 64: Issues
The usage for this system is very low
Small system with little penetration
Oversized system – battery usage

## Slide 65: Load Curve for Mini-Grid
The Load curve shows that there is potentially high variability in this system that was not apparent in the other systems.
Note how the load decreased for the recent period relative to the initial period.

## Slide 66: Estimated Energy Consumption
Energy consumption is less for the Muite. Note the decline after the initial free electricity. The base is about 50kWh/day. 50 kWh/day. Per month this is 1,500 kWh (about the size of a suburban home in the US). Per year the demand is 18,250 kWh.

## Slide 67: Muite PVGIS
.

## Slide 68: Solar Peak Production and Performance Ratio
Less Date for this system. If produce 70 when the irradiation is 1,000 watts/m2 then as the capacity is 130.8, the implied performance ratio is only 53%.

## Slide 69: Hourly Solar Production
Produced 80 kW of solar with capacity of 130.8. Implies a performance ratio of 61%. The shape implies that there is wasted solar and the maximum may be constrained by the battery capacity and the load.

## Slide 70: Temperature on Panels and Simulation
.

## Slide 71: Problem of Oversizing and Surplus Capacity
.

## Slide 72: Muite Tariff
.

## Slide 73: Cash Flow with Over-sizing
.

## Slide 74: Cost Estimates

## Slide 75: Objectives
Should reflect reasonable estimates of costs for new system
Incorporate different methods for computing distribution costs
Begin with assumptions used for existing systems
Must be able to evaluate rapidly changing solar and battery costs
Must be able to simulate diesel costs with different fuel prices

## Slide 76: Nigeria Model
.

## Slide 77: Source 4: Current Estimates from Asia
Cost of Solar
  USD 63/kW for panels
  USD 360/kW for system including inverter
Cost of Battery
  USD 130/kWh including inverter

## Slide 78: Generation Costs in UIPCE Report
Data provided by private sector and programmes. Regional benchmarks for “best in class” systems
Minimum connections: 150
Production costs:
Solar system: $1,500/kW
Battery: $530/kWh
Inverter: $304/kW
Diesel generator set: $371/kVA
Wind turbine: $2,500/kW
Hydro: $14,588/kW

## Slide 79: Generation Costs in Regulatory Report
.

## Slide 80: Inputs for Generation Costs
.

## Slide 81: Distribution Costs
"Forced" grid length: 30km & < 2,000 $/connection
Maximum grid branch: 150km
Central grid CAPEX: 2500 $/kW
Distribution costs:
Medium Voltage: 26,000 $/km
Low Voltage: 18,900 $/km
Transformers: 29,200 $/160 kVA
Grid losses: 15%
Disc rate: 8%

## Slide 82: Distribution Capital Costs and Connection Cost from Regulatory Report
Distribution
Cost
1 phase 6,000 MZN
3 phases (industrial customers only) 12,000 MZN
Cost per connection 8,000 MZN

## Slide 83: Generic Mini-Grid From Regulatory
Electricity produced per year Unit
One village 50,000 kWh
Portfolio size 30 mini-grids
Entire portfolio 1,500,000 kWh
Equity Expected ROI before taxes (%) 18%
Debt interest rate 14%
Loan term (years) 10
FOREX MZN-USD 62
Cost of diesel (MZN/Unit) 71.71 MZN

## Slide 84: Operating and Maintenance Cost from Regulatory Report
Total cost including cost of solar and insurance.

## Slide 85: Inputs for Distribution Capital Expenditures
.

## Slide 86: Tariffs and Grant

## Slide 87: Tariffs

## Slide 88: Tariffs for Households

## Slide 89: Other Tariffs
.

## Slide 90: Other Tariffs Continued
.

## Slide 91: Project Fact Sheet
Project start year 2024
Own funds on total investment at project start 5%
CAPEX subsidy 80%
Own funds at component replacement 70%
Equity Expected ROI before taxes (%) 18%
Debt interest rate 14%
Loan term (years) 10
FOREX MZN-USD 62

## Slide 92: Need for GCF – Private Operators do Not Make a Profit

## Slide 93: Potential for GCF
.

## Slide 94: Alternative (Negative) Case

## Slide 95: Location of Mini-grid
.

## Slide 96: Demand and Supply Reduction – What is the Cause
.

## Slide 97: Is the Decline in Solar Production for Consumption Due to Decline in Demand or Problems with Solar Farm
.

## Slide 98: Alto Changane – Demand Reduction or Battery Degradation
.

## Slide 99: Round Trip Efficiency Percent
.

## Slide 100: Loss Percent
.

## Slide 101: Subsidy and Model Development
Evaluate existing subsidies and cash flow from the model
25 MZM/kWh = 40 US Cents/kWh

## Slide 102: Appendix – Computation of Solar Output and Battery Discharge

## Slide 103: Inputs from PVSYST Example
.
33,008 meters for 6.784 MWp or 33,008/6.784; 4,865 m2 per MWp; Football field assumptions – 50 x 150 meters = 7,500 m2. 1 MW is 4865/7,500 = .64% of a football field. Or, 7,500/4865 = 1.54 means a football field gives you 1.54 MWp.
5,120 MWac
6,784 MWp
75% Ratio

## Slide 104: Loss Factors in PVSYST
To understand solar I think you should replicate PVSYST by yourself.
You need data on the various loss factors, the temperature coefficient and the AC/DC Ratio

## Slide 105: Performance Ratio by Month
.
Capacity for Radiation on Plane – 2,458 kWh per m2. With STC of 1,000 the capacity factor is 28.06%
Final Capacity factor. Generation kWh is 13,064. Capacity in MWP is 6,784, Average Production is 1,491 kWh. Capacity Factor is 21.97%.
Performance Ratio is Final Capacity Factor Divided by Gross or
21.97% divided by 28.06% or 78.3%

## Slide 106: Capacity Factor for Solar with Performance Ratio and Temperature - Equations

## Slide 107: Idea that cannot use Ambient Temperature
.

## Slide 108: Solar, Temperature and Performance Ratio
Temperature coefficient
Note that 20 to 30 degrees above the ambient temperature

## Slide 109: Detailed Weather Measurement

## Slide 110: Detailed Solar Analysis with Temperature Adjustment
.
Find the file named hourly equations

## Slide 111: Providing PVSYST Report in PPA
.

## Slide 112: Detailed Formulas for Solar with Performance Ratio
Soiling Losses = Soiling Percent x In Plane Radiation
Net In Plance radiation = Gross In-plane Radiation – Soiling Losses
Pantel Temperatre Adjustment = 3% x Gross In Plane Radiation
Temperature on Pantel = Temperature + Panel Adjustment Temperature
Temperature versus STC Temperature = Temperature – Temperature on Panel
Efficiency Effect of Temp = Temperature Coefficient x Temperature Difference
Temperature Effect = Efficiency Adjustment * In Plane Radiation
Subtotal = Irritation – Losses – Temperature Effect
Other Losses = Other Loss Percent x Other Loss Percent
Subtotal = subtotal – Other Losses
Irradiation STC = 1000
AC/DC ratio = AC percent x ADC
Output before Loss = Minimum (AC Output, subtotal)
Inverter Loss = Output before loss x Inverter Loss Percent
Compute financial capacity factor as percent of STC

## Slide 113: Incorporate Detail of Solar
Add 15 columns
Soiling Loss Assumption: 2.8%
Factor for Increase in Temperature on Panel (% of irradiation) – 3%
Temperature Coefficient Percent Efficiency/(Panel Temp-25): -.41%
Other Wiring Losses: 2.9%
AC to DC ratio: 80%
Inverter Losses: 3%

## Slide 114: Cell Panel Temperature from Ambient Temperature
Use Homer Method with 3%
Note that results in 20 to 30 degree adjustments.

## Slide 115: Temperature Adjustment with Temperature Coefficient
Use PV adjustment of -.4%
Note that never come close to 1,000 STC; this is reason for the AC/DC ratio

## Slide 116: AC to DC Ratio and Performance Ratio
Can compute the remaining output subject to the maximum output from the size of the inverter

## Slide 117: Size of System
.

## Slide 118: Capital Expenditure Discussion
.

## Slide 119
One of the pending points are the mini-grid construction milestones that would result in the disbursement of a percentage of the CAPEX support funds to the SPVs.
One variant could be to define in advance very strict milestone moments that will be applied for all SPVs or as the other variant, the definition of these milestones could be kept very open and be the result of negotiations with the SPVs during the concession awarding.
Of course, the final decision is with Enabel, but based on your experience with GCF, would both variants be acceptable for GCF?
In which sense does the decision on the construction milestones influence the financial model of annex 3?