{"text_format":"1","workbook":"xlsx","n_sheets":18,"sheets":["Alpha","Summary","Power Curve Comparison","Two Power Curves","All Power Curves","Nordex 6.8 Mode 1","Mode 7","Mode 8","Mode 9","Mode 0","Mode 3","Mode 6","Vestas PO7","Vestas 6.1 SO1","Vestas 5.2 SO2","Vestas 4.8 SO4","Enercon Mode 0","Enercon 2"],"not_rendered":{"charts":5,"images":6,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[{"sheet":"Power Curve Comparison","index":2,"reason":"not_a_worksheet"},{"sheet":"Two Power Curves","index":3,"reason":"not_a_worksheet"}],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Alpha","index":0,"n_rows":42,"n_cols":23,"rows_kept":42,"cut":false,"hidden":false,"merged":[]}
[]
[null,"Height","Average Wind Speed","A-Parameter","k-Parameter","Brutto-wind-energie [kWh/m²]","Yield","Height Ratio","Wind Speed Ratio","Log of Height Ratio","Log of Height Ratio","Implied Alpha","10 Meter Speed","Check of Wind Speed"]
[null,5,3.35,3.7,1.65,484,4254]
[null,10,3.92,4.4000000000000004,1.74,724,6497,{"$f":"B4/$B$4","v":1},{"$f":"C4/$C$4","v":1},{"$f":"LN(H4)","v":0},{"$f":"LN(I4)","v":0},{"$f":"IF(J4,K4/J4)","v":false},null,null,null,null,null,"v2/v1 = [z2/z1]^ a"]
[null,15,4.26,4.8,1.79,896,8026,{"$f":"B5/$B$4","v":1.5},{"$f":"C5/$C$4","v":1.0867346938775511},{"$f":"LOG10(H5)","v":0.17609125905568124},{"$f":"LOG(I5)","v":3.612353208226169E-2},{"$f":"IF(J5,K5/J5)","v":0.20514097222076871},{"$f":"$C$4","v":3.92},{"$f":"(H5^L5)*M5","v":4.26}]
[null,20,4.49,5.0999999999999996,1.82,1032,9182,2,1.1454081632653061,{"$f":"LOG10(H6)","v":0.3010299956639812},{"$f":"LOG(I6)","v":5.8960273982865935E-2},0.19586179062593875,{"$f":"$C$4","v":3.92},{"$f":"(H6^L6)*M6","v":4.49},null,null,null,"log (v2/v1]= a * log(z2/z1)"]
[null,25,4.67,5.3,1.85,1144,10113,2.5,1.1913265306122449,0.3979400086720376,7.6030813545654927E-2,0.19106099384019401,3.92,4.67,null,null,null,"a = log(v2/v1)/log(z2/z1)"]
[null,30,4.8499999999999996,5.5,1.89,1248,10994,3,1.2372448979591837,0.47712125471966244,9.2455671581806412E-2,0.19377814479493208,3.92,4.8499999999999996]
[null,35,5,5.6,1.92,1340,11758,3.5,1.2755102040816326,0.54406804435027567,0.10568393731556155,0.19424764680265127,3.92,5,null,null,null,"v2 ",6.23]
[null,40,5.13,5.8,1.96,1423,12437,4,1.3086734693877551,0.6020599913279624,0.11683129809135902,0.19405258574592291,3.92,5.13,null,null,null,"v1",3.92]
[null,45,5.25,5.9,1.98,1498,13050,4.5,1.3392857142857144,0.65321251377534373,0.12687323638549966,0.19422964764134107,3.92,5.25]
[null,50,5.35,6,2.0099999999999998,1568,13606,5,1.3647959183673468,0.69897000433601886,0.13506771500077117,0.19323821360414128,3.92,5.35,null,null,null,"z2",100]
[null,55,5.47,6.2,2.0299999999999998,1658,14302,5.5,1.3954081632653061,0.74036268949424389,0.14470125931297353,0.19544644991743407,3.92,5.47,null,null,null,"z1",10]
[null,60,5.58,6.3,2.0499999999999998,1740,14948,6,1.4234693877551021,0.77815125038364363,0.15334813191712152,0.19706725632262098,3.92,5.58]
[null,65,5.68,6.4,2.0699999999999998,1820,15550,6.5,1.4489795918367347,0.81291335664285558,0.16106226869056164,0.19812968673034431,3.92,5.68,null,null,null,"z2/z1",{"$f":"S12/S13","v":10}]
[null,70,5.78,6.5,2.09,1897,16112,7,1.4744897959183674,0.84509804001425681,0.1686417714000718,0.19955290796465083,3.92,5.78,null,null,null,"LN",{"$f":"LN(S15)","v":2.3025850929940459},null,null,"z2",300]
[null,75,5.86,6.6,2.1,1970,16640,7.5,1.4948979591836735,0.87506126339170009,0.17461154899763343,0.19954208499739381,3.92,5.86,null,null,null,"Log 10",{"$f":"LOG10(S15)","v":1},null,null,"z1",150]
[null,80,5.95,6.7,2.12,2039,17138,8,1.517857142857143,0.90308998699194354,0.18123089870809236,0.20067867136003262,3.92,5.95,null,null,null,"Log",{"$f":"LOG(S15)","v":1},null,null,"z2/z1",{"$f":"W16/W17","v":2}]
[null,85,6.02,6.8,2.13,2103,17607,8.5,1.5357142857142856,0.92941892571429274,0.18631042423736727,0.20045903852687402,3.92,6.02]
[null,90,6.09,6.9,2.15,2168,18054,9,1.5535714285714286,0.95424250943932487,0.19133122561241811,0.20050587111743404,3.92,6.09,null,null,null,"v2/v1",{"$f":"S9/S10","v":1.5892857142857144}]
[null,95,6.16,7,2.16,2230,18476,9.5,1.5714285714285714,0.97772360528884772,0.19629464514396819,0.20076701031062566,3.92,6.16,null,null,null,"LN",{"$f":"LN(S20)","v":0.46328467899699066},null,null,"v2",8.6]
[null,100,6.23,7,2.17,2289,18881,10,1.5892857142857144,1,0.20120197963871239,0.20120197963871239,3.92,6.23,null,null,null,"Log 10",{"$f":"LOG10(S20)","v":0.20120197963871239},null,null,"v1",6.83]
[null,105,6.32,7.1,2.17,2390,19465,10.5,1.6122448979591837,1.0211892990699381,0.20743101126192778,0.20312689474013132,3.92,6.32,null,null,null,"Log",{"$f":"LOG(S20)","v":0.20120197963871239},null,null,"v2/v1",{"$f":"W21/W22","v":1.2591508052708638}]
[null,110,6.4,7.2,2.16,2489,20016,11,1.6326530612244898,1.0413926851582251,0.21289390696342994,0.2044319208282932,3.92,6.4]
[null,115,6.48,7.3,2.16,2587,20541,11.5,1.653061224489796,1.0606978403536116,0.21828893885013612,0.2057974764777156,3.92,6.48,null,null,null,"alpha ln",{"$f":"S21/S16","v":0.20120197963871236},null,null,"ln(z2/z1)",{"$f":"LN(W18)","v":0.69314718055994529}]
[null,120,6.56,7.4,2.15,2683,21040,12,1.6734693877551019,1.0791812460476249,0.223617772355203,0.20721058040452142,3.92,6.56,null,null,null,"alpha log",{"$f":"S22/S17","v":0.20120197963871239},null,null,"ln(v2/v1)",{"$f":"LN(W23)","v":0.23043752967676329}]
[null,125,6.63,7.5,2.15,2773,21513,12.5,1.6913265306122449,1.0969100130080565,0.22822746138431591,0.20806397851948466,3.92,6.63]
[null,130,6.7,7.6,2.15,2871,21964,13,1.7091836734693879,1.1139433523068367,0.23278873568036923,0.20897717572288843,3.92,6.7,null,null,null,"z2/z1 ^ a",{"$f":"S15^S25","v":1.5892857142857144},null,null,"alpha",{"$f":"W26/W25","v":0.33245108129936973}]
[null,135,6.77,7.6,2.15,2956,22388,13.5,1.7270408163265305,1.1303337684950061,0.23730260166468703,0.20994029222062957,3.92,6.77,null,null,null,"z2/z1 ^ a",{"$f":"S15^S26","v":1.5892857142857144}]
[null,140,6.83,7.7,2.14,3045,22790,14,1.7423469387755102,1.146128035678238,0.24113463666107532,0.21039066243448132,3.92,6.830000000000001]
[null,145,6.89,7.8,2.14,3131,23174,14.5,1.7576530612244898,1.1613680022349748,0.24493315488716857,0.21090055384323586,3.92,6.89,null,null,null,"Result",{"$f":"S29*S10","v":6.23}]
[null,150,6.95,7.9,2.14,3212,23543,15,1.7729591836734695,1.1760912590556813,0.24869873756965666,0.21146210862016293,3.92,6.9499999999999993]
[null,155,7.01,7.9,2.13,3297,23898,15.5,1.7882653061224489,1.1903316981702914,0.25243195094620141,0.21206857830823553,3.92,7.0100000000000007]
[null,160,7.07,8,2.13,3375,24238,16,1.8035714285714286,1.2041199826559248,0.25613334677644217,0.21271414017354767,3.92,7.07]
[null,165,7.12,8,2.13,3457,24565,16.5,1.8163265306122449,1.2174839442139063,0.25919392661639912,0.21289309633052536,3.92,7.12]
[null,170,7.18,8.1,2.13,3533,24881,17,1.8316326530612244,1.2304489213782739,0.26283837722184306,0.21361177425181332,3.92,7.18]
[null,175,7.23,8.1999999999999993,2.13,3613,25182,17.5,1.8443877551020409,1.2430380486862944,0.26585223027407362,0.21387296274240336,3.92,7.2300000000000013]
[null,180,7.28,8.1999999999999993,2.13,3686,25475,18,1.8571428571428572,1.255272505103306,0.26884531229257996,0.21417286780327799,3.92,7.28]
[null,185,7.32,8.3000000000000007,2.12,3763,25754,18.5,1.8673469387755104,1.2671717284030137,0.27122501403793464,0.21403966641502731,3.92,7.3199999999999994]
[null,190,7.37,8.3000000000000007,2.12,3834,26026,19,1.8801020408163267,1.2787536009528289,0.27418142083859426,0.21441301954832842,3.92,7.37]
[null,195,7.42,8.4,2.12,3903,26286,19.5,1.8928571428571428,1.2900346113625181,0.27711783825856984,0.21481426608072285,3.92,7.4200000000000008]
[null,200,7.46,8.4,2.12,3978,26538,20,1.903061224489796,1.3010299956639813,0.27945276045221157,0.21479348007621663,3.92,7.4599999999999991]

{"sheet":"Summary","index":1,"n_rows":74,"n_cols":31,"rows_kept":74,"cut":false,"hidden":false,"merged":[]}
[]
[null,null,null,null,10,7]
[null,null,null,null,null,null,null,"Nordex Mode1","Nordex Mode7","Nordex Mode8","Nordex Mode9","Nordex Mode0","Nordex Mode3","Nordex Mode6","Vestas PO7","Vestas 6.1","Vestas SO4","Enercon Mode 0","Enercon 2","Nordex Mode1","Nordex Mode7","Nordex Mode8","Nordex Mode9","Nordex Mode0","Nordex Mode3","Nordex Mode6","Vestas PO7","Vestas 6.1","Vestas SO4","Enercon Mode 0","Enercon 2"]
[]
[null,null,null,null,{"$f":"INDEX(T5:AE5,$E$2)","v":"Vestas SO4"},{"$f":"INDEX(T5:AF5,$F$2)","v":"Nordex Mode6"},"Wind Speed","Power P (kW)","Power P (kW)","Power P (kW)","Power P (kW)","Power P (kW)","Power P (kW)","Power P (kW)","Power P (kW)","Power (kW)","Power P (kW)","Power P (kW)","P_v (kW)","Nordex Mode1","Nordex Mode7","Nordex Mode8","Nordex Mode9","Nordex Mode0","Nordex Mode3","Nordex Mode6","Vestas PO7","Vestas 6.1","Vestas SO4","Enercon Mode 0","Enercon 2"]
[null,null,null,0,{"$f":"INDEX(T6:AE6,$E$2)","v":0},{"$f":"INDEX(T6:AF6,$F$2)","v":0},0,0,0,0,0,0,0,0,0,0,0,0,0,{"$f":"H6/MAX(H$6:H$56)","v":0},{"$f":"I6/MAX(I$6:I$56)","v":0},{"$f":"J6/MAX(J$6:J$56)","v":0},0,0,0,0,0,0,0,0,0]
[null,null,null,0.5,{"$f":"INDEX(T7:AE7,$E$2)","v":0},{"$f":"INDEX(T7:AF7,$F$2)","v":0},0.5,0,0,0,0,0,0,0,0,0,0,0,0,{"$f":"H7/MAX(H$6:H$56)","v":0},0,0,0,0,0,0,0,0,0,0,0]
[null,null,null,1,{"$f":"INDEX(T8:AE8,$E$2)","v":0},{"$f":"INDEX(T8:AF8,$F$2)","v":0},1,0,0,0,0,0,0,0,0,0,0,1,0,0,0,0,0,0,0,0,0,0,0,4.8780487804878049E-4,0]
[null,null,null,1.5,{"$f":"INDEX(T9:AE9,$E$2)","v":0},{"$f":"INDEX(T9:AF9,$F$2)","v":0},1.5,0,0,0,0,0,0,0,0,0,0,1.7320508075688772,0,0,0,0,0,0,0,0,0,0,0,8.4490283296042787E-4,0]
[null,null,null,2,{"$f":"INDEX(T10:AE10,$E$2)","v":0},{"$f":"INDEX(T10:AF10,$F$2)","v":0},2,0,0,0,0,0,0,0,0,0,0,3,0,0,0,0,0,0,0,0,0,0,0,1.4634146341463415E-3,0]
[null,null,null,2.5,{"$f":"INDEX(T11:AE11,$E$2)","v":0},{"$f":"INDEX(T11:AF11,$F$2)","v":0},2.5,0,0,0,0,0,0,0,0,0,0,8.6602540378443873,10,0,0,0,0,0,0,0,0,0,0,4.2245141648021402E-3,4.2553191489361703E-3]
[null,null,null,3,{"$f":"INDEX(T12:AE12,$E$2)","v":6.1538461538461538E-3},{"$f":"INDEX(T12:AF12,$F$2)","v":1.3051146384479718E-2},3,45,45,45,45,74,74,74,32,32,32,25,25,6.6176470588235293E-3,7.575757575757576E-3,7.7319587628865982E-3,8.5388994307400382E-3,1.088235294117647E-2,1.2191103789126854E-2,1.3051146384479718E-2,4.4444444444444444E-3,5.2459016393442623E-3,6.1538461538461538E-3,1.2195121951219513E-2,1.0638297872340425E-2]
[null,null,null,3.5,{"$f":"INDEX(T13:AE13,$E$2)","v":2.4807692307692308E-2},{"$f":"INDEX(T13:AF13,$F$2)","v":3.439153439153439E-2},3.5,150,150,150,150,195,195,195,129,129,129,45.276925690687079,49,2.2058823529411766E-2,2.5252525252525252E-2,2.5773195876288658E-2,2.8462998102466792E-2,2.8676470588235293E-2,3.2125205930807248E-2,3.439153439153439E-2,1.7916666666666668E-2,2.1147540983606557E-2,2.4807692307692308E-2,2.2086305214969307E-2,2.0851063829787235E-2]
[null,null,null,4,{"$f":"INDEX(T14:AE14,$E$2)","v":5.5384615384615386E-2},{"$f":"INDEX(T14:AF14,$F$2)","v":6.3492063492063489E-2},4,291,291,291,291,360,360,360,288,288,288,82,82,4.2794117647058823E-2,4.8989898989898993E-2,0.05,5.5218216318785582E-2,5.2941176470588235E-2,5.9308072487644151E-2,6.3492063492063489E-2,0.04,4.7213114754098361E-2,5.5384615384615386E-2,0.04,3.4893617021276593E-2]
[null,null,null,4.5,{"$f":"INDEX(T15:AE15,$E$2)","v":9.0576923076923083E-2},{"$f":"INDEX(T15:AF15,$F$2)","v":0.1},4.5,465,465,465,465,567,567,567,481,471,471,119.44873377311289,123,6.8382352941176477E-2,7.8282828282828287E-2,7.9896907216494839E-2,8.8235294117647065E-2,8.3382352941176477E-2,9.3410214168039532E-2,0.1,6.6805555555555562E-2,7.7213114754098366E-2,9.0576923076923083E-2,5.8267675011274583E-2,5.2340425531914897E-2]
[null,null,null,5,{"$f":"INDEX(T16:AE16,$E$2)","v":0.13403846153846155},{"$f":"INDEX(T16:AF16,$F$2)","v":0.1437389770723104},5,674,674,674,674,815,815,815,715,698,697,174,174,9.9117647058823533E-2,0.11346801346801347,0.11580756013745705,0.12789373814041746,0.11985294117647059,0.13426688632619441,0.1437389770723104,9.930555555555555E-2,0.11442622950819673,0.13403846153846155,8.4878048780487811E-2,7.4042553191489363E-2]
[null,null,null,5.5,{"$f":"INDEX(T17:AE17,$E$2)","v":0.18730769230769231},{"$f":"INDEX(T17:AF17,$F$2)","v":0.19576719576719576},5.5,921,921,921,921,1110,1110,1110,999,974,974,236.33450869477358,240,0.13544117647058823,0.15505050505050505,0.15824742268041236,0.17476280834914612,0.16323529411764706,0.18286655683690281,0.19576719576719576,0.13875000000000001,0.15967213114754097,0.18730769230769231,0.11528512619257247,0.10212765957446808]
[null,null,null,6,{"$f":"INDEX(T18:AE18,$E$2)","v":0.25134615384615383},{"$f":"INDEX(T18:AF18,$F$2)","v":0.25731922398589063},6,1214,1214,1214,1215,1458,1458,1459,1340,1307,1307,321,321,0.17852941176470588,0.20437710437710438,0.20859106529209623,0.23055028462998103,0.21441176470588236,0.24019769357495882,0.25731922398589063,0.18611111111111112,0.2142622950819672,0.25134615384615383,0.15658536585365854,0.13659574468085106]
[null,null,null,6.5,{"$f":"INDEX(T19:AE19,$E$2)","v":0.32634615384615384},{"$f":"INDEX(T19:AF19,$F$2)","v":0.32945326278659615},6.5,1559,1559,1559,1555,1868,1868,1868,1739,1697,1697,413.24568963269297,418,0.22926470588235295,0.26245791245791245,0.26786941580756013,0.29506641366223907,0.27470588235294119,0.30774299835255353,0.32945326278659615,0.24152777777777779,0.27819672131147544,0.32634615384615384,0.20158326323546,0.17787234042553191]
[null,null,null,7,{"$f":"INDEX(T20:AE20,$E$2)","v":0.41365384615384615},{"$f":"INDEX(T20:AF20,$F$2)","v":0.41340388007054674},7,1960,1960,1959,1919,2344,2344,2344,2203,2150,2151,532,532,0.28823529411764703,0.32996632996632996,0.33659793814432992,0.36413662239089184,0.3447058823529412,0.38616144975288302,0.41340388007054674,0.3059722222222222,0.35245901639344263,0.41365384615384615,0.25951219512195123,0.22638297872340427]
[null,null,null,7.5,{"$f":"INDEX(T21:AE21,$E$2)","v":0.5130769230769231},{"$f":"INDEX(T21:AF21,$F$2)","v":0.50670194003527336},7.5,2420,2406,2396,2277,2891,2891,2873,2729,2666,2668,658.46791873256814,664,0.35588235294117648,0.40505050505050505,0.41168384879725084,0.43206831119544592,0.42514705882352943,0.47627677100494231,0.50670194003527336,0.3790277777777778,0.43704918032786882,0.5130769230769231,0.3212038627963747,0.2825531914893617]
[null,null,null,8,{"$f":"INDEX(T22:AE22,$E$2)","v":0.62057692307692303},{"$f":"INDEX(T22:AF22,$F$2)","v":0.60246913580246919},8,2944,2865,2837,2614,3509,3494,3416,3324,3251,3227,815,815,0.43294117647058822,0.48232323232323232,{"$f":"J22/MAX(J$6:J$56)","v":0.48745704467353951},{"$f":"K22/MAX(K$6:K$56)","v":0.49601518026565466},{"$f":"L22/MAX(L$6:L$56)","v":0.51602941176470585},{"$f":"M22/MAX(M$6:M$56)","v":0.57561779242174627},{"$f":"N22/MAX(N$6:N$56)","v":0.60246913580246919},{"$f":"O22/MAX(O$6:O$56)","v":0.46166666666666667},{"$f":"P22/MAX(P$6:P$56)","v":0.53295081967213109},{"$f":"Q22/MAX(Q$6:Q$56)","v":0.62057692307692303},{"$f":"R22/MAX(R$6:R$56)","v":0.39756097560975612},{"$f":"S22/MAX(S$6:S$56)","v":0.34680851063829787}]
[null,null,null,8.5,{"$f":"INDEX(T23:AE23,$E$2)","v":0.72692307692307689},{"$f":"INDEX(T23:AF23,$F$2)","v":0.69647266313932976},8.5,3520,3313,3264,2921,4163,4112,3949,3986,3903,3780,980.66304100848004,988,0.51764705882352946,0.55774410774410776,0.56082474226804124,0.55426944971537007,0.61220588235294116,0.67742998352553541,0.69647266313932976,0.55361111111111116,0.63983606557377048,0.72692307692307689,0.4783722151260878,0.42042553191489362]
[null,null,null,9,{"$f":"INDEX(T24:AE24,$E$2)","v":0.82711538461538459},{"$f":"INDEX(T24:AF24,$F$2)","v":0.78536155202821867},9,4115,3736,3662,3203,4815,4719,4453,4685,4570,4301,1180,1180,0.60514705882352937,0.62895622895622894,0.62920962199312713,0.6077798861480076,0.70808823529411768,0.77742998352553538,0.78536155202821867,0.65069444444444446,0.74918032786885247,0.82711538461538459,0.57560975609756093,0.50212765957446803]
[null,null,null,9.5,{"$f":"INDEX(T25:AE25,$E$2)","v":0.92057692307692307},{"$f":"INDEX(T25:AF25,$F$2)","v":0.86172839506172838},9.5,4701,4124,4025,3471,5437,5224,4886,5314,5206,4787,1365.4303350958628,1384,0.69132352941176467,0.69427609427609427,0.69158075601374569,0.65863377609108165,0.79955882352941177,0.86062602965403623,0.86172839506172838,0.73805555555555558,0.85344262295081963,0.92057692307692307,0.66606357809554284,0.58893617021276601]
[null,null,null,10,{"$f":"INDEX(T26:AE26,$E$2)","v":1},{"$f":"INDEX(T26:AF26,$F$2)","v":0.91746031746031742},10,5267,4483,4364,3731,5940,5590,5202,5904,5774,5200,1580,1580,0.77455882352941174,0.75471380471380467,0.74982817869415808,0.70796963946869074,0.87352941176470589,0.92092257001647448,0.91746031746031742,0.82,0.9465573770491803,1,0.77073170731707319,0.67234042553191486]
[null,null,null,10.5,{"$f":"INDEX(T27:AE27,$E$2)","v":1},{"$f":"INDEX(T27:AF27,$F$2)","v":0.95661375661375658},10.5,5771,4824,4688,3980,6304,5836,5424,6441,6100,5200,1691.0943202553785,1749,0.84867647058823525,0.81212121212121213,0.80549828178694161,0.75521821631878561,0.92705882352941171,0.96144975288303125,0.95661375661375658,0.89458333333333329,1,1,0.82492405866116025,0.74425531914893617]
[null,null,null,11,{"$f":"INDEX(T28:AE28,$E$2)","v":1},{"$f":"INDEX(T28:AF28,$F$2)","v":0.98165784832451497},11,6148,5140,4996,4217,6549,5987,5566,6854,6100,5200,1810,1890,0.90411764705882358,0.86531986531986527,0.85841924398625424,0.80018975332068309,0.96308823529411769,0.98632619439868208,0.98165784832451497,0.95194444444444448,1,1,0.88292682926829269,0.80425531914893622]
[null,null,null,11.5,{"$f":"INDEX(T29:AE29,$E$2)","v":1},{"$f":"INDEX(T29:AF29,$F$2)","v":0.99523809523809526},11.5,6421,5398,5254,4445,6703,6056,5643,7078,6100,5200,1893.0927077140202,2005,0.94426470588235289,0.90875420875420876,0.9027491408934708,0.84345351043643269,0.98573529411764704,0.99769357495881383,0.99523809523809526,0.98305555555555557,1,1,0.9234598574214733,0.85319148936170208]
[null,null,null,12,{"$f":"INDEX(T30:AE30,$E$2)","v":1},{"$f":"INDEX(T30:AF30,$F$2)","v":1},12,6611,5595,5453,4663,6780,6070,5670,7160,6100,5200,1980,2100,0.97220588235294114,0.94191919191919193,0.93694158075601375,0.88481973434535099,0.99705882352941178,1,1,0.99444444444444446,1,1,0.96585365853658534,0.8936170212765957]
[null,null,null,12.5,{"$f":"INDEX(T31:AE31,$E$2)","v":1},{"$f":"INDEX(T31:AF31,$F$2)","v":1},12.5,6731,5741,5603,4845,6800,6070,5670,7195,6100,5200,2014.6960068456976,2180,0.9898529411764706,0.96649831649831652,0.96271477663230243,0.91935483870967738,1,1,1,0.99930555555555556,1,1,0.98277853992473052,0.92765957446808511]
[null,null,null,13,{"$f":"INDEX(T32:AE32,$E$2)","v":1},{"$f":"INDEX(T32:AF32,$F$2)","v":1},13,6791,5844,5710,4985,6800,6070,5670,7200,6100,5200,2050,2250,0.99867647058823528,0.98383838383838385,0.98109965635738827,0.9459203036053131,1,1,1,1,1,1,1,0.95744680851063835]
[null,null,null,13.5,{"$f":"INDEX(T33:AE33,$E$2)","v":1},{"$f":"INDEX(T33:AF33,$F$2)","v":1},13.5,6800,5907,5779,5091,6800,6070,5670,7200,6100,5200,2050,2311,1,0.99444444444444446,0.99295532646048112,0.96603415559772299,1,1,1,1,1,1,1,0.98340425531914899]
[null,null,null,14,{"$f":"INDEX(T34:AE34,$E$2)","v":1},{"$f":"INDEX(T34:AF34,$F$2)","v":1},14,6800,5935,5813,5169,6800,6070,5670,7200,6100,5200,2050,2350,1,0.99915824915824913,0.99879725085910653,0.98083491461100569,1,1,1,1,1,1,1,1]
[null,null,null,14.5,{"$f":"INDEX(T35:AE35,$E$2)","v":1},{"$f":"INDEX(T35:AF35,$F$2)","v":1},14.5,6800,5940,5820,5225,6800,6070,5670,7200,6100,5200,2050,2350,1,1,1,0.99146110056925996,1,1,1,1,1,1,1,1]
[null,null,null,15,{"$f":"INDEX(T36:AE36,$E$2)","v":1},{"$f":"INDEX(T36:AF36,$F$2)","v":1},15,6800,5940,5820,5258,6800,6070,5670,7200,6100,5200,2050,2350,1,1,1,0.99772296015180262,1,1,1,1,1,1,1,1]
[null,null,null,15.5,{"$f":"INDEX(T37:AE37,$E$2)","v":1},{"$f":"INDEX(T37:AF37,$F$2)","v":1},15.5,6800,5940,5820,5270,6800,6070,5670,7200,6100,5200,2050,2350,1,1,1,1,1,1,1,1,1,1,1,1]
[null,null,null,16,{"$f":"INDEX(T38:AE38,$E$2)","v":1},{"$f":"INDEX(T38:AF38,$F$2)","v":1},16,6800,5940,5820,5270,6793,6070,5670,7200,6100,5200,2050,2350,1,1,1,1,0.99897058823529417,1,1,1,1,1,1,1]
[null,null,null,16.5,{"$f":"INDEX(T39:AE39,$E$2)","v":0.9653846153846154},{"$f":"INDEX(T39:AF39,$F$2)","v":1},16.5,6800,5940,5820,5270,6752,6070,5670,7200,5887,5020,2050,2350,1,1,1,1,0.99294117647058822,1,1,1,0.96508196721311479,0.9653846153846154,1,1]
[null,null,null,17,{"$f":"INDEX(T40:AE40,$E$2)","v":0.93057692307692308},{"$f":"INDEX(T40:AF40,$F$2)","v":1},17,6800,5940,5820,5270,6705,6070,5670,7200,5674,4839,2050,2350,1,1,1,1,0.98602941176470593,1,1,1,0.93016393442622947,0.93057692307692308,1,1]
[null,null,null,17.5,{"$f":"INDEX(T41:AE41,$E$2)","v":0.89596153846153848},{"$f":"INDEX(T41:AF41,$F$2)","v":1},17.5,6800,5940,5820,5270,6589,6070,5670,7194,5461,4659,2050,2350,1,1,1,1,0.96897058823529414,1,1,0.99916666666666665,0.89524590163934425,0.89596153846153848,1,1]
[null,null,null,18,{"$f":"INDEX(T42:AE42,$E$2)","v":0.86134615384615387},{"$f":"INDEX(T42:AF42,$F$2)","v":1},18,6800,5940,5820,5270,6453,6070,5670,7124,5248,4479,2050,2350,1,1,1,1,0.94897058823529412,1,1,0.98944444444444446,0.86032786885245904,0.86134615384615387,1,1]
[null,null,null,18.5,{"$f":"INDEX(T43:AE43,$E$2)","v":0.82653846153846156},{"$f":"INDEX(T43:AF43,$F$2)","v":1},18.5,6800,5940,5820,5270,6256,6070,5670,6959,5035,4298,2050,2350,1,1,1,1,0.92,1,1,0.96652777777777776,0.82540983606557372,0.82653846153846156,1,1]
[null,null,null,19,{"$f":"INDEX(T44:AE44,$E$2)","v":0.79192307692307695},{"$f":"INDEX(T44:AF44,$F$2)","v":1},19,6800,5940,5820,5270,6045,6017,5670,6789,4822,4118,2050,2350,1,1,1,1,0.88897058823529407,0.99126853377265234,1,0.94291666666666663,0.79049180327868851,0.79192307692307695,1,1]
[null,null,null,19.5,{"$f":"INDEX(T45:AE45,$E$2)","v":0.75730769230769235},{"$f":"INDEX(T45:AF45,$F$2)","v":0.99911816578483248},19.5,6800,5940,5820,5270,5855,5855,5665,6630,4609,3938,2050,2350,1,1,1,1,0.86102941176470593,0.96457990115321257,0.99911816578483248,0.92083333333333328,0.7555737704918033,0.75730769230769235,1,1]
[null,null,null,20,{"$f":"INDEX(T46:AE46,$E$2)","v":0.72250000000000003},{"$f":"INDEX(T46:AF46,$F$2)","v":0.99541446208112871},20,6800,5940,5820,5270,5644,5644,5644,6472,4396,3757,2050,2350,1,1,1,1,0.83,0.92981878088962111,0.99541446208112871,0.89888888888888885,0.72065573770491809,0.72250000000000003,1,1]
[null,null,null,20.5,{"$f":"INDEX(T47:AE47,$E$2)","v":0.68788461538461543},{"$f":"INDEX(T47:AF47,$F$2)","v":0},20.5,6603,null,null,5270,null,null,null,6262,4183,3577,2050,2350,0.97102941176470592,0,0,1,0,0,0,0.86972222222222217,0.68573770491803276,0.68788461538461543,1,1]
[null,null,null,21,{"$f":"INDEX(T48:AE48,$E$2)","v":0.65326923076923082},{"$f":"INDEX(T48:AF48,$F$2)","v":0},21,6331,null,null,5270,null,null,null,5946,3970,3397,2050,2350,0.93102941176470588,0,0,1,0,0,0,0.82583333333333331,0.65081967213114755,0.65326923076923082,1,1]
[null,null,null,21.5,{"$f":"INDEX(T49:AE49,$E$2)","v":0.61846153846153851},{"$f":"INDEX(T49:AF49,$F$2)","v":0},21.5,6059,null,null,5270,null,null,null,5538,3757,3216,2050,2350,0.89102941176470585,0,0,1,0,0,0,0.76916666666666667,0.61590163934426234,0.61846153846153851,1,1]
[null,null,null,22,{"$f":"INDEX(T50:AE50,$E$2)","v":0.58384615384615379},{"$f":"INDEX(T50:AF50,$F$2)","v":0},22,5794,null,null,5270,null,null,null,5069,3544,3036,2050,2350,0.85205882352941176,0,0,1,0,0,0,0.70402777777777781,0.58098360655737702,0.58384615384615379,1,1]
[null,null,null,22.5,{"$f":"INDEX(T51:AE51,$E$2)","v":0.54923076923076919},{"$f":"INDEX(T51:AF51,$F$2)","v":0},22.5,5528,null,null,5270,null,null,null,4597,3331,2856,2050,2350,0.81294117647058828,0,0,1,0,0,0,0.63847222222222222,0.54606557377049181,0.54923076923076919,1,1]
[null,null,null,23,{"$f":"INDEX(T52:AE52,$E$2)","v":0.51442307692307687},{"$f":"INDEX(T52:AF52,$F$2)","v":0},23,5270,null,null,5270,null,null,null,4121,3118,2675,2050,2350,0.77500000000000002,0,0,1,0,0,0,0.5723611111111111,0.5111475409836066,0.51442307692307687,1,1]
[null,null,null,23.5,{"$f":"INDEX(T53:AE53,$E$2)","v":0.47980769230769232},{"$f":"INDEX(T53:AF53,$F$2)","v":0},23.5,5012,null,null,5012,null,null,null,3636,2905,2495,2050,2346,0.73705882352941177,0,0,0.95104364326375712,0,0,0,0.505,0.47622950819672133,0.47980769230769232,1,0.99829787234042555]
[null,null,null,24,{"$f":"INDEX(T54:AE54,$E$2)","v":0.44519230769230766},{"$f":"INDEX(T54:AF54,$F$2)","v":0},24,4760,null,null,4760,null,null,null,3169,2692,2315,2050,2339,0.7,0,0,0.90322580645161288,0,0,0,0.44013888888888891,0.44131147540983606,0.44519230769230766,1,0.99531914893617024]
[null,null,null,24.5,{"$f":"INDEX(T55:AE55,$E$2)","v":0.4103846153846154},{"$f":"INDEX(T55:AF55,$F$2)","v":0},24.5,4508,null,null,4508,null,null,null,2718,2479,2134,2050,2350,0.66294117647058826,0,0,0.85540796963946875,0,0,0,0.3775,0.4063934426229508,0.4103846153846154,1,1]
[null,null,null,25,{"$f":"INDEX(T56:AE56,$E$2)","v":0.37576923076923074},{"$f":"INDEX(T56:AF56,$F$2)","v":0},25,4264,null,null,4264,null,null,null,2328,2266,1954,2050,null,0.62705882352941178,0,0,0.80910815939278935,0,0,0,0.32333333333333331,0.37147540983606558,0.37576923076923074,1,0]
[]
[]
[]
[]
[]
[]
[null,null,null,null,{"$f":"TRANSPOSE(H3:S3)","v":"Nordex Mode1"}]
[null,null,null,null,"Nordex Mode7"]
[null,null,null,null,"Nordex Mode8"]
[null,null,null,null,"Nordex Mode9"]
[null,null,null,null,"Nordex Mode0"]
[null,null,null,null,"Nordex Mode3"]
[null,null,null,null,"Nordex Mode6"]
[null,null,null,null,"Vestas PO7"]
[null,null,null,null,"Vestas 6.1"]
[null,null,null,null,"Vestas SO4"]
[null,null,null,null,"Enercon Mode 0"]
[null,null,null,null,"Enercon 2"]

{"sheet":"All Power Curves","index":4,"n_rows":56,"n_cols":62,"rows_kept":56,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,null,"Nordex Mode1","Nordex Mode1","Nordex Mode1",null,null,"Nordex Mode7","Nordex Mode7",null,null,null,"Nordex Mode8","Nordex Mode8",null,null,null,"Nordex Mode9","Nordex Mode9",null,null,null,"Nordex Mode0","Nordex Mode0",null,null,null,null,"Nordex Mode3","Nordex Mode3",null,null,null,"Nordex Mode6","Nordex Mode6",null,null,null,"Vestas PO7","Vestas PO7",null,null,null,"Vestas 6.1","Vestas 6.1",null,null,"Vestas SO4","Vestas SO4",null,null,null,null,"Enercon Mode 0","Enercon Mode 0",null,null,null,null,null,null,"Enercon 2"]
[]
[null,null,"Wind Speed v (m/s) for Power","Power P (kW)","Wind Speed v (m/s) for Ct","Thrust Coefficient Ct",null,"Wind Speed v (m/s) for Power","Power P (kW)","Wind Speed v (m/s) for Ct","Thrust Coefficient Ct",null,"Wind Speed v (m/s) for Power","Power P (kW)","Wind Speed v (m/s) for Ct","Thrust Coefficient Ct",null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct",null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct",null,null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct",null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct",null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct",null,"Wind Speed (m/s)","Power (kW)","Thrust Coefficient (Ct)",null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct",null,null,null,"Wind Speed v (m/s) for Power","Power P (kW)","Wind Speed v (m/s) for Ct","Thrust Coefficient Ct",null,null,"v (m/s)","P_v (kW)"]
[null,null,0,null,null,null,null,0,null,null,null,null,0,null,null,null,null,0,null,null,null,null,0,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"C6","v":0},{"$f":"interpolate_look_up(BA6,BC:BC,BD:BD)","v":0},0,null,null,null,null,null,0,0]
[null,null,0.5,null,null,null,null,0.5,null,null,null,null,0.5,null,null,null,null,0.5,null,null,null,null,0.5,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"C7","v":0.5},{"$f":"interpolate_look_up(BA7,BC:BC,BD:BD)","v":0},1,1,1,0,null,null,0.5,0]
[null,null,1,null,null,null,null,1,null,null,null,null,1,null,null,null,null,1,null,null,null,null,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,{"$f":"interpolate_look_up(BA8,BC:BC,BD:BD)","v":1},2,3,2,0.78100000000000003,null,null,1,0]
[null,null,1.5,null,null,null,null,1.5,null,null,null,null,1.5,null,null,null,null,1.5,null,null,null,null,1.5,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5,{"$f":"interpolate_look_up(BA9,BC:BC,BD:BD)","v":1.7320508075688772},3,25,3,0.78500000000000003,null,null,1.5,0]
[null,null,2,null,null,null,null,2,null,null,null,null,2,null,null,null,null,2,null,null,null,null,2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2,{"$f":"interpolate_look_up(BA10,BC:BC,BD:BD)","v":3},4,82,4,0.77400000000000002,null,null,2,0]
[null,null,2.5,null,null,null,null,2.5,null,null,null,null,2.5,null,null,null,null,2.5,null,null,null,null,2.5,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.5,{"$f":"interpolate_look_up(BA11,BC:BC,BD:BD)","v":8.6602540378443873},5,174,5,0.78100000000000003,null,null,2.5,10]
[null,null,3,45,{"$f":"C12","v":3},0.89200000000000002,null,3,45,{"$f":"H12","v":3},0.89200000000000002,null,3,45,3,0.89200000000000002,null,3,45,3,0.89200000000000002,null,3,74,3,0.874,null,null,3,74,3,0.874,null,3,74,3,0.874,null,3,32,3,0.96899999999999997,null,3,32,0.96899999999999997,null,3,32,3,0.96899999999999997,null,3,{"$f":"interpolate_look_up(BA12,BC:BC,BD:BD)","v":25},6,321,6,0.77700000000000002,null,null,3,25]
[null,null,3.5,150,{"$f":"C13","v":3.5},0.86599999999999999,null,3.5,150,{"$f":"H13","v":3.5},0.86599999999999999,null,3.5,150,3.5,0.86599999999999999,null,3.5,150,3.5,0.86599999999999999,null,3.5,195,3.5,0.86699999999999999,null,null,3.5,195,3.5,0.86699999999999999,null,3.5,195,3.5,0.86699999999999999,null,3.5,129,3.5,0.88500000000000001,null,3.5,129,0.88500000000000001,null,3.5,129,3.5,0.88500000000000001,null,3.5,{"$f":"interpolate_look_up(BA13,BC:BC,BD:BD)","v":45.276925690687079},7,532,7,0.77800000000000002,null,null,3.5,49]
[null,null,4,291,{"$f":"C14","v":4},0.84499999999999997,null,4,291,4,0.84499999999999997,null,4,291,4,0.84499999999999997,null,4,291,4,0.84499999999999997,null,4,360,4,0.85199999999999998,null,null,4,360,4,0.85199999999999998,null,4,360,4,0.85199999999999998,null,4,288,4,0.83399999999999996,null,4,288,0.83099999999999996,null,4,288,4,0.83199999999999996,null,4,{"$f":"interpolate_look_up(BA14,BC:BC,BD:BD)","v":82},8,815,8,0.77500000000000002,null,null,4,82]
[null,null,4.5,465,{"$f":"C15","v":4.5},0.83,null,4.5,465,4.5,0.83,null,4.5,465,4.5,0.83,null,4.5,465,4.5,0.83,null,4.5,567,4.5,0.83899999999999997,null,null,4.5,567,4.5,0.83899999999999997,null,4.5,567,4.5,0.83899999999999997,null,4.5,481,4.5,0.81799999999999995,null,4.5,471,0.81699999999999995,null,4.5,471,4.5,0.81599999999999995,null,4.5,{"$f":"interpolate_look_up(BA15,BC:BC,BD:BD)","v":119.44873377311289},9,1180,9,0.76900000000000002,null,null,4.5,123]
[null,null,5,674,{"$f":"C16","v":5},0.82,null,5,674,5,0.82,null,5,674,5,0.82,null,5,674,5,0.82,null,5,815,5,0.83,null,null,5,815,5,0.83,null,5,815,5,0.83,null,5,715,5,0.81200000000000006,null,5,698,0.81200000000000006,null,5,697,5,0.81200000000000006,null,5,{"$f":"interpolate_look_up(BA16,BC:BC,BD:BD)","v":174},10,1580,10,0.77,null,null,5,174]
[null,null,5.5,921,{"$f":"C17","v":5.5},0.81399999999999995,null,5.5,921,5.5,0.81399999999999995,null,5.5,921,5.5,0.81399999999999995,null,5.5,921,5.5,0.81399999999999995,null,5.5,1110,5.5,0.82399999999999995,null,null,5.5,1110,5.5,0.82399999999999995,null,5.5,1110,5.5,0.82399999999999995,null,5.5,999,5.5,0.81499999999999995,null,5.5,974,0.81399999999999995,null,5.5,974,5.5,0.81399999999999995,null,5.5,{"$f":"interpolate_look_up(BA17,BC:BC,BD:BD)","v":236.33450869477358},11,1810,11,0.77300000000000002,null,null,5.5,240]
[null,null,6,1214,{"$f":"C18","v":6},0.80900000000000005,null,6,1214,6,0.80900000000000005,null,6,1214,6,0.80900000000000005,null,6,1215,6,0.79900000000000004,null,6,1458,6,0.82,null,null,6,1458,6,0.82,null,6,1459,6,0.82,null,6,1340,6,0.81399999999999995,null,6,1307,0.81399999999999995,null,6,1307,6,0.81399999999999995,null,6,{"$f":"interpolate_look_up(BA18,BC:BC,BD:BD)","v":321},12,1980,12,0.495,null,null,6,321]
[null,null,6.5,1559,{"$f":"C19","v":6.5},0.80600000000000005,null,6.5,1559,6.5,0.80400000000000005,null,6.5,1559,6.5,0.8,null,6.5,1555,6.5,0.76700000000000002,null,6.5,1868,6.5,0.81699999999999995,null,null,6.5,1868,6.5,0.81699999999999995,null,6.5,1868,6.5,0.81399999999999995,null,6.5,1739,6.5,0.81,null,6.5,1697,0.81100000000000005,null,6.5,1697,6.5,0.81100000000000005,null,6.5,{"$f":"interpolate_look_up(BA19,BC:BC,BD:BD)","v":413.24568963269297},13,2050,13,0.36699999999999999,null,null,6.5,418]
[null,null,7,1960,{"$f":"C20","v":7},0.80600000000000005,null,7,1960,7,0.78500000000000003,null,7,1959,7,0.77700000000000002,null,7,1919,7,0.72399999999999998,null,7,2344,7,0.81599999999999995,null,null,7,2344,7,0.81200000000000006,null,7,2344,7,0.79300000000000004,null,7,2203,7,0.80500000000000005,null,7,2150,0.80600000000000005,null,7,2151,7,0.80600000000000005,null,7,{"$f":"interpolate_look_up(BA20,BC:BC,BD:BD)","v":532},14,2050,14,0.28599999999999998,null,null,7,532]
[null,null,7.5,2420,{"$f":"C21","v":7.5},0.80100000000000005,null,7.5,2406,7.5,0.753,null,7.5,2396,7.5,0.74199999999999999,null,7.5,2277,7.5,0.67600000000000005,null,7.5,2891,7.5,0.80400000000000005,null,null,7.5,2891,7.5,0.79300000000000004,null,7.5,2873,7.5,0.76200000000000001,null,7.5,2729,7.5,0.79700000000000004,null,7.5,2666,0.79900000000000004,null,7.5,2668,7.5,0.79900000000000004,null,7.5,{"$f":"interpolate_look_up(BA21,BC:BC,BD:BD)","v":658.46791873256814},15,2050,15,0.23,null,null,7.5,664]
[null,null,8,2944,{"$f":"C22","v":8},0.78400000000000003,null,8,2865,8,0.71499999999999997,null,8,2837,8,0.70099999999999996,null,8,2614,8,0.624,null,8,3509,8,0.77900000000000003,null,null,8,3494,8,0.76400000000000001,null,8,3416,8,0.72299999999999998,null,8,3324,8,0.78800000000000003,null,8,3251,0.79100000000000004,null,8,3227,8,0.78700000000000003,null,8,{"$f":"interpolate_look_up(BA22,BC:BC,BD:BD)","v":815},16,2050,16,0.188,null,null,8,815]
[null,null,8.5,3520,{"$f":"C23","v":8.5},0.75800000000000001,null,8.5,3313,8.5,0.67100000000000004,null,8.5,3264,8.5,0.65600000000000003,null,8.5,2921,8.5,0.57199999999999995,null,8.5,4163,8.5,0.747,null,null,8.5,4112,8.5,0.72399999999999998,null,8.5,3949,8.5,0.67800000000000005,null,8.5,3986,8.5,0.77700000000000002,null,8.5,3903,0.77400000000000002,null,8.5,3780,8.5,0.747,null,8.5,{"$f":"interpolate_look_up(BA23,BC:BC,BD:BD)","v":980.66304100848004},17,2050,17,0.156,null,null,8.5,988]
[null,null,9,4115,{"$f":"C24","v":9},0.72499999999999998,null,9,3736,9,0.625,null,9,3662,9,0.60899999999999999,null,9,3203,9,0.52,null,9,4815,9,0.70499999999999996,null,null,9,4719,9,0.67500000000000004,null,9,4453,9,0.627,null,9,4685,9,0.75,null,9,4570,0.73099999999999998,null,9,4301,9,0.69099999999999995,null,9,{"$f":"interpolate_look_up(BA24,BC:BC,BD:BD)","v":1180},18,2050,18,0.13100000000000001,null,null,9,1180]
[null,null,9.5,4701,{"$f":"C25","v":9.5},0.68700000000000006,null,9.5,4124,9.5,0.57899999999999996,null,9.5,4025,9.5,0.56200000000000006,null,9.5,3471,9.5,0.47,null,9.5,5437,9.5,0.65600000000000003,null,null,9.5,5224,9.5,0.621,null,9.5,4886,9.5,0.57299999999999995,null,9.5,5314,9.5,0.69,null,9.5,5206,0.67500000000000004,null,9.5,4787,9.5,0.63200000000000001,null,9.5,{"$f":"interpolate_look_up(BA25,BC:BC,BD:BD)","v":1365.4303350958628},19,2050,19,0.111,null,null,9.5,1384]
[null,null,10,5267,{"$f":"C26","v":10},0.64200000000000002,null,10,4483,10,0.53200000000000003,null,10,4364,10,0.51500000000000001,null,10,3731,10,0.42299999999999999,null,10,5940,10,0.60499999999999998,null,null,10,5590,10,0.56699999999999995,null,10,5202,10,0.51800000000000002,null,10,5904,10,0.628,null,10,5774,0.61599999999999999,null,10,5200,10,0.57499999999999996,null,10,{"$f":"interpolate_look_up(BA26,BC:BC,BD:BD)","v":1580},20,2050,20,9.6000000000000002E-2,null,null,10,1580]
[null,null,10.5,5771,{"$f":"C27","v":10.5},0.59499999999999997,null,10.5,4824,10.5,0.48399999999999999,null,10.5,4688,10.5,0.46800000000000003,null,10.5,3980,10.5,0.38300000000000001,null,10.5,6304,10.5,0.55200000000000005,null,null,10.5,5836,10.5,0.51200000000000001,null,10.5,5424,10.5,0.46400000000000002,null,10.5,6441,10.5,0.57099999999999995,null,10.5,6100,0.55000000000000004,null,10.5,5200,10.5,0.51400000000000001,null,10.5,{"$f":"interpolate_look_up(BA27,BC:BC,BD:BD)","v":1691.0943202553785},21,2050,21,8.4000000000000005E-2,null,null,10.5,1749]
[null,null,11,6148,{"$f":"C28","v":11},0.54600000000000004,null,11,5140,11,0.438,null,11,4996,11,0.42299999999999999,null,11,4217,11,0.34799999999999998,null,11,6549,11,0.5,null,null,11,5987,11,0.45900000000000002,null,11,5566,11,0.41299999999999998,null,11,6854,11,0.51300000000000001,null,11,6100,0.48199999999999998,null,11,5200,11,0.45100000000000001,null,11,{"$f":"interpolate_look_up(BA28,BC:BC,BD:BD)","v":1810},22,2050,22,7.3999999999999996E-2,null,null,11,1890]
[null,null,11.5,6421,{"$f":"C29","v":11.5},0.498,null,11.5,5398,11.5,0.39500000000000002,null,11.5,5254,11.5,0.38200000000000001,null,11.5,4445,11.5,0.317,null,11.5,6703,11.5,0.45,null,null,11.5,6056,11.5,0.40799999999999997,null,11.5,5643,11.5,0.36699999999999999,null,11.5,7078,11.5,0.45100000000000001,null,11.5,6100,0.41599999999999998,null,11.5,5200,11.5,0.39200000000000002,null,11.5,{"$f":"interpolate_look_up(BA29,BC:BC,BD:BD)","v":1893.0927077140202},23,2050,23,6.6000000000000003E-2,null,null,11.5,2005]
[null,null,12,6611,{"$f":"C30","v":12},0.45,null,12,5595,12,0.35699999999999998,null,12,5453,12,0.34599999999999997,null,12,4663,12,0.28899999999999998,null,12,6780,12,0.40100000000000002,null,null,12,6070,12,0.36199999999999999,null,12,5670,12,0.32700000000000001,null,12,7160,12,0.39200000000000002,null,12,6100,0.36099999999999999,null,12,5200,12,0.34200000000000003,null,12,{"$f":"interpolate_look_up(BA30,BC:BC,BD:BD)","v":1980},24,2050,24,5.8999999999999997E-2,null,null,12,2100]
[null,null,12.5,6731,{"$f":"C31","v":12.5},0.40500000000000003,null,12.5,5741,12.5,0.32400000000000001,null,12.5,5603,12.5,0.313,null,12.5,4845,12.5,0.26300000000000001,null,12.5,6800,12.5,0.35799999999999998,null,null,12.5,6070,12.5,0.32100000000000001,null,12.5,5670,12.5,0.29099999999999998,null,12.5,7195,12.5,0.34100000000000003,null,12.5,6100,0.314,null,12.5,5200,12.5,0.3,null,12.5,{"$f":"interpolate_look_up(BA31,BC:BC,BD:BD)","v":2014.6960068456976},25,2050,25,5.2999999999999999E-2,null,null,12.5,2180]
[null,null,13,6791,{"$f":"C32","v":13},0.36399999999999999,null,13,5844,13,0.29299999999999998,null,13,5710,13,0.28399999999999997,null,13,4985,13,0.24,null,13,6800,13,0.31900000000000001,null,null,13,6070,13,0.28399999999999997,null,13,5670,13,0.25900000000000001,null,13,7200,13,0.29899999999999999,null,13,6100,0.27500000000000002,null,13,5200,13,0.26400000000000001,null,13,{"$f":"interpolate_look_up(BA32,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,13,2250]
[null,null,13.5,6800,{"$f":"C33","v":13.5},0.32700000000000001,null,13.5,5907,13.5,0.26600000000000001,null,13.5,5779,13.5,0.25800000000000001,null,13.5,5091,13.5,0.22,null,13.5,6800,13.5,0.28399999999999997,null,null,13.5,6070,13.5,0.251,null,13.5,5670,13.5,0.23100000000000001,null,13.5,7200,13.5,0.26400000000000001,null,13.5,6100,0.24299999999999999,null,13.5,5200,13.5,0.23400000000000001,null,13.5,{"$f":"interpolate_look_up(BA33,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,13.5,2311]
[null,null,14,6800,{"$f":"C34","v":14},0.29499999999999998,null,14,5935,14,0.24199999999999999,null,14,5813,14,0.23499999999999999,null,14,5169,14,0.20100000000000001,null,14,6800,14,0.253,null,null,14,6070,14,0.223,null,14,5670,14,0.20599999999999999,null,14,7200,14,0.23499999999999999,null,14,6100,0.217,null,14,5200,14,0.20799999999999999,null,14,{"$f":"interpolate_look_up(BA34,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,14,2350]
[null,null,14.5,6800,{"$f":"C35","v":14.5},0.26500000000000001,null,14.5,5940,14.5,0.22,null,14.5,5820,14.5,0.214,null,14.5,5225,14.5,0.184,null,14.5,6800,14.5,0.22600000000000001,null,null,14.5,6070,14.5,0.19900000000000001,null,14.5,5670,14.5,0.184,null,14.5,7200,14.5,0.21,null,14.5,6100,0.19400000000000001,null,14.5,5200,14.5,0.186,null,14.5,{"$f":"interpolate_look_up(BA35,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,14.5,2350]
[null,null,15,6800,{"$f":"C36","v":15},0.23899999999999999,null,15,5940,15,0.2,null,15,5820,15,0.19500000000000001,null,15,5258,15,0.16900000000000001,null,15,6800,15,0.20200000000000001,null,null,15,6070,15,0.17899999999999999,null,15,5670,15,0.16500000000000001,null,15,7200,15,0.188,null,15,6100,0.17399999999999999,null,15,5200,15,0.16700000000000001,null,15,{"$f":"interpolate_look_up(BA36,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,15,2350]
[null,null,15.5,6800,{"$f":"C37","v":15.5},0.215,null,15.5,5940,15.5,0.182,null,15.5,5820,15.5,0.17799999999999999,null,15.5,5270,15.5,0.155,null,15.5,6800,15.5,0.182,null,null,15.5,6070,15.5,0.161,null,15.5,5670,15.5,0.14899999999999999,null,15.5,7200,15.5,0.17,null,15.5,6100,0.158,null,15.5,5200,15.5,0.15,null,15.5,{"$f":"interpolate_look_up(BA37,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,15.5,2350]
[null,null,16,6800,{"$f":"C38","v":16},0.193,null,16,5940,16,0.16600000000000001,null,16,5820,16,0.16200000000000001,null,16,5270,16,0.14299999999999999,null,16,6793,16,0.16500000000000001,null,null,16,6070,16,0.14599999999999999,null,16,5670,16,0.13500000000000001,null,16,7200,16,0.155,null,16,6100,0.14299999999999999,null,16,5200,16,0.13700000000000001,null,16,{"$f":"interpolate_look_up(BA38,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,16,2350]
[null,null,16.5,6800,{"$f":"C39","v":16.5},0.17599999999999999,null,16.5,5940,16.5,0.151,null,16.5,5820,16.5,0.14799999999999999,null,16.5,5270,16.5,0.13100000000000001,null,16.5,6752,16.5,0.15,null,null,16.5,6070,16.5,0.13300000000000001,null,16.5,5670,16.5,0.123,null,16.5,7200,16.5,0.14099999999999999,null,16.5,5887,0.13,null,16.5,5020,16.5,0.124,null,16.5,{"$f":"interpolate_look_up(BA39,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,16.5,2350]
[null,null,17,6800,{"$f":"C40","v":17},0.161,null,17,5940,17,0.13900000000000001,null,17,5820,17,0.13600000000000001,null,17,5270,17,0.122,null,17,6705,17,0.13600000000000001,null,null,17,6070,17,0.12,null,17,5670,17,0.111,null,17,7200,17,0.129,null,17,5674,0.11899999999999999,null,17,4839,17,0.113,null,17,{"$f":"interpolate_look_up(BA40,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,17,2350]
[null,null,17.5,6800,{"$f":"C41","v":17.5},0.14899999999999999,null,17.5,5940,17.5,0.128,null,17.5,5820,17.5,0.125,null,17.5,5270,17.5,0.113,null,17.5,6589,17.5,0.124,null,null,17.5,6070,17.5,0.11,null,17.5,5670,17.5,0.10100000000000001,null,17.5,7194,17.5,0.11899999999999999,null,17.5,5461,0.109,null,17.5,4659,17.5,0.104,null,17.5,{"$f":"interpolate_look_up(BA41,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,17.5,2350]
[null,null,18,6800,{"$f":"C42","v":18},0.13800000000000001,null,18,5940,18,0.11899999999999999,null,18,5820,18,0.11700000000000001,null,18,5270,18,0.105,null,18,6453,18,0.113,null,null,18,6070,18,0.1,null,18,5670,18,9.2999999999999999E-2,null,18,7124,18,0.108,null,18,5248,0.1,null,18,4479,18,9.6000000000000002E-2,null,18,{"$f":"interpolate_look_up(BA42,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,18,2350]
[null,null,18.5,6800,{"$f":"C43","v":18.5},0.129,null,18.5,5940,18.5,0.112,null,18.5,5820,18.5,0.109,null,18.5,5270,18.5,9.9000000000000005E-2,null,18.5,6256,18.5,0.10299999999999999,null,null,18.5,6070,18.5,9.0999999999999998E-2,null,18.5,5670,18.5,8.4000000000000005E-2,null,18.5,6959,18.5,9.8000000000000004E-2,null,18.5,5035,9.1999999999999998E-2,null,18.5,4298,18.5,8.7999999999999995E-2,null,18.5,{"$f":"interpolate_look_up(BA43,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,18.5,2350]
[null,null,19,6800,{"$f":"C44","v":19},0.122,null,19,5940,19,0.105,null,19,5820,19,0.10299999999999999,null,19,5270,19,9.2999999999999999E-2,null,19,6045,19,9.2999999999999999E-2,null,null,19,6017,19,8.2000000000000003E-2,null,19,5670,19,7.5999999999999998E-2,null,19,6789,19,8.7999999999999995E-2,null,19,4822,8.5000000000000006E-2,null,19,4118,19,8.1000000000000003E-2,null,19,{"$f":"interpolate_look_up(BA44,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,19,2350]
[null,null,19.5,6800,{"$f":"C45","v":19.5},0.115,null,19.5,5940,19.5,0.1,null,19.5,5820,19.5,9.8000000000000004E-2,null,19.5,5270,19.5,8.7999999999999995E-2,null,19.5,5855,19.5,8.5999999999999993E-2,null,null,19.5,5855,19.5,7.5999999999999998E-2,null,19.5,5665,19.5,7.0000000000000007E-2,null,19.5,6630,19.5,0.08,null,19.5,4609,7.8E-2,null,19.5,3938,19.5,7.4999999999999997E-2,null,19.5,{"$f":"interpolate_look_up(BA45,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,19.5,2350]
[null,null,20,6800,{"$f":"C46","v":20},0.11,null,20,5940,20,9.5000000000000001E-2,null,20,5820,20,9.2999999999999999E-2,null,20,5270,20,8.4000000000000005E-2,null,20,5644,20,7.9000000000000001E-2,null,null,20,5644,20,7.0000000000000007E-2,null,20,5644,20,6.5000000000000002E-2,null,20,6472,20,7.2999999999999995E-2,null,20,4396,7.1999999999999995E-2,null,20,3757,20,7.0000000000000007E-2,null,20,{"$f":"interpolate_look_up(BA46,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,20,2350]
[null,null,20.5,6603,{"$f":"C47","v":20.5},9.9000000000000005E-2,null,null,null,null,null,null,null,null,null,null,null,20.5,5270,20.5,7.5999999999999998E-2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,20.5,6262,20.5,6.6000000000000003E-2,null,20.5,4183,6.5000000000000002E-2,null,20.5,3577,20.5,6.4000000000000001E-2,null,20.5,{"$f":"interpolate_look_up(BA47,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,20.5,2350]
[null,null,21,6331,{"$f":"C48","v":21},8.8999999999999996E-2,null,null,null,null,null,null,null,null,null,null,null,21,5270,21,6.8000000000000005E-2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,21,5946,21,5.8000000000000003E-2,null,21,3970,5.8000000000000003E-2,null,21,3397,21,5.8000000000000003E-2,null,21,{"$f":"interpolate_look_up(BA48,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,21,2350]
[null,null,21.5,6059,{"$f":"C49","v":21.5},0.08,null,null,null,null,null,null,null,null,null,null,null,21.5,5270,21.5,6.0999999999999999E-2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,21.5,5538,21.5,5.1999999999999998E-2,null,21.5,3757,5.0999999999999997E-2,null,21.5,3216,21.5,5.0999999999999997E-2,null,21.5,{"$f":"interpolate_look_up(BA49,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,21.5,2350]
[null,null,22,5794,{"$f":"C50","v":22},7.1999999999999995E-2,null,null,null,null,null,null,null,null,null,null,null,22,5270,22,5.5E-2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,22,5069,22,4.4999999999999998E-2,null,22,3544,4.3999999999999997E-2,null,22,3036,22,4.3999999999999997E-2,null,22,{"$f":"interpolate_look_up(BA50,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,22,2350]
[null,null,22.5,5528,{"$f":"C51","v":22.5},6.4000000000000001E-2,null,null,null,null,null,null,null,null,null,null,null,22.5,5270,22.5,4.9000000000000002E-2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,22.5,4597,22.5,3.9E-2,null,22.5,3331,3.7999999999999999E-2,null,22.5,2856,22.5,3.7999999999999999E-2,null,22.5,{"$f":"interpolate_look_up(BA51,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,22.5,2350]
[null,null,23,5270,{"$f":"C52","v":23},5.8000000000000003E-2,null,null,null,null,null,null,null,null,null,null,null,23,5270,23,4.3999999999999997E-2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,23,4121,23,3.3000000000000002E-2,null,23,3118,3.3000000000000002E-2,null,23,2675,23,3.3000000000000002E-2,null,23,{"$f":"interpolate_look_up(BA52,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,23,2350]
[null,null,23.5,5012,{"$f":"C53","v":23.5},5.1999999999999998E-2,null,null,null,null,null,null,null,null,null,null,null,23.5,5012,23.5,3.9E-2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,23.5,3636,23.5,2.8000000000000001E-2,null,23.5,2905,2.8000000000000001E-2,null,23.5,2495,23.5,2.8000000000000001E-2,null,23.5,{"$f":"interpolate_look_up(BA53,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,23.5,2346]
[null,null,24,4760,{"$f":"C54","v":24},4.5999999999999999E-2,null,null,null,null,null,null,null,null,null,null,null,24,4760,24,3.5000000000000003E-2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,24,3169,24,2.4E-2,null,24,2692,2.4E-2,null,24,2315,24,2.4E-2,null,24,{"$f":"interpolate_look_up(BA54,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,24,2339]
[null,null,24.5,4508,{"$f":"C55","v":24.5},4.2000000000000003E-2,null,null,null,null,null,null,null,null,null,null,null,24.5,4508,24.5,3.2000000000000001E-2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,24.5,2718,24.5,0.02,null,24.5,2479,0.02,null,24.5,2134,24.5,0.02,null,24.5,{"$f":"interpolate_look_up(BA55,BC:BC,BD:BD)","v":2050},null,null,null,null,null,null,24.5,2350]
[null,null,25,4264,{"$f":"C56","v":25},3.7999999999999999E-2,null,null,null,null,null,null,null,null,null,null,null,25,4264,25,2.9000000000000001E-2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,25,2328,25,1.7000000000000001E-2,null,25,2266,1.7000000000000001E-2,null,25,1954,25,1.7000000000000001E-2,null,25,{"$f":"interpolate_look_up(BA56,BC:BC,BD:BD)","v":2050}]

{"sheet":"Nordex 6.8 Mode 1","index":5,"n_rows":52,"n_cols":10,"rows_kept":52,"cut":false,"hidden":false,"merged":[]}
[]
[null,null,null,null,null,null,null,null,null,"13.4.1 Nordex N163/6.X (6.8 MW) Betriebsmodus Mode 1"]
[]
[]
[null,"Windgeschwindigkeit v (m/s)","Leistung P (kW)","Schubbeiwert Ct"]
[null,3,45,0.89200000000000002,null,3,45,0.89200000000000002]
[null,3.5,150,0.86599999999999999,null,3.5,150,0.86599999999999999]
[null,4,291,0.84499999999999997,null,4,291,0.84499999999999997]
[null,4.5,465,0.83,null,4.5,465,0.83]
[null,5,674,0.82,null,5,674,0.82]
[null,5.5,921,0.81399999999999995,null,5.5,921,0.81399999999999995]
[null,6,1214,0.80900000000000005,null,6,1214,0.80900000000000005]
[null,6.5,1559,0.80600000000000005,null,6.5,1559,0.80600000000000005]
[null,7,1960,0.80600000000000005,null,7,1960,0.80600000000000005]
[null,7.5,2420,0.80100000000000005,null,7.5,2420,0.80100000000000005]
[null,8,2944,0.78400000000000003,null,8,2944,0.78400000000000003]
[null,8.5,3520,0.75800000000000001,null,8.5,3520,0.75800000000000001]
[null,9,4115,0.72499999999999998,null,9,4115,0.72499999999999998]
[null,9.5,4701,0.68700000000000006,null,9.5,4701,0.68700000000000006]
[null,10,5267,0.64200000000000002,null,10,5267,0.64200000000000002]
[null,10.5,5771,0.59499999999999997,null,10.5,5771,0.59499999999999997]
[null,11,6148,0.54600000000000004,null,11,6148,0.54600000000000004]
[null,11.5,6421,0.498,null,11.5,6421,0.498]
[null,12,6611,0.45,null,12,6611,0.45]
[null,12.5,6731,0.40500000000000003,null,12.5,6731,0.40500000000000003]
[null,13,6791,0.36399999999999999,null,13,6791,0.36399999999999999]
[null,13.5,6800,0.32700000000000001,null,13.5,6800,0.32700000000000001]
[null,14,6800,0.29499999999999998,null,14,6800,0.29499999999999998]
[null,14.5,6800,0.26500000000000001,null,14.5,6800,0.26500000000000001]
[null,15,6800,0.23899999999999999,null,15,6800,0.23899999999999999]
[null,15.5,6800,0.215,null,15.5,6800,0.215]
[null,16,6800,0.193,null,16,6800,0.193]
[null,16.5,6800,0.17599999999999999,null,16.5,6800,0.17599999999999999]
[null,17,6800,0.161,null,17,6800,0.161]
[null,17.5,6800,0.14899999999999999,null,17.5,6800,0.14899999999999999]
[null,18,6800,0.13800000000000001,null,18,6800,0.13800000000000001]
[null,18.5,6800,0.129,null,18.5,6800,0.129]
[null,19,6800,0.122,null,19,6800,0.122]
[null,19.5,6800,0.115,null,19.5,6800,0.115]
[null,20,6800,0.11,null,20,6800,0.11]
[null,20.5,6603,9.9000000000000005E-2,null,20.5,6603,9.9000000000000005E-2]
[null,21,6331,8.8999999999999996E-2,null,21,6331,8.8999999999999996E-2]
[null,21.5,6059,0.08,null,21.5,6059,0.08]
[null,22,5794,7.1999999999999995E-2,null,22,5794,7.1999999999999995E-2]
[null,22.5,5528,6.4000000000000001E-2,null,22.5,5528,6.4000000000000001E-2]
[null,23,5270,5.8000000000000003E-2,null,23,5270,5.8000000000000003E-2]
[null,23.5,5012,5.1999999999999998E-2,null,23.5,5012,5.1999999999999998E-2]
[null,24,4760,4.5999999999999999E-2,null,24,4760,4.5999999999999999E-2]
[null,24.5,4508,4.2000000000000003E-2,null,24.5,4508,4.2000000000000003E-2]
[null,25,4264,3.7999999999999999E-2,null,25,4264,3.7999999999999999E-2]
[null,25.5,4019,3.5000000000000003E-2,null,25.5,4019,3.5000000000000003E-2]
[null,26,3774,3.2000000000000001E-2,null,26,3774,3.2000000000000001E-2]

{"sheet":"Mode 7","index":6,"n_rows":39,"n_cols":5,"rows_kept":39,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,"Wind Speed v (m/s)","Calculated Power P (kW)","Thrust Coefficient Ct","Notes / Status"]
[null,3,45,0.89200000000000002,"Available"]
[null,3.5,150,0.86599999999999999,"Available"]
[null,4,291,0.84499999999999997,"Available"]
[null,4.5,465,0.83,"Available"]
[null,5,674,0.82,"Available"]
[null,5.5,921,0.81399999999999995,"Available"]
[null,6,1214,0.80900000000000005,"Available"]
[null,6.5,1559,0.80400000000000005,"Available"]
[null,7,1960,0.78500000000000003,"Available"]
[null,7.5,2406,0.753,"Available"]
[null,8,2865,0.71499999999999997,"Available"]
[null,8.5,3313,0.67100000000000004,"Available"]
[null,9,3736,0.625,"Available"]
[null,9.5,4124,0.57899999999999996,"Available"]
[null,10,4483,0.53200000000000003,"Available"]
[null,10.5,4824,0.48399999999999999,"Available"]
[null,11,5140,0.438,"Available"]
[null,11.5,5398,0.39500000000000002,"Available"]
[null,12,5595,0.35699999999999998,"Available"]
[null,12.5,5741,0.32400000000000001,"Available"]
[null,13,5844,0.29299999999999998,"Available"]
[null,13.5,5907,0.26600000000000001,"Available"]
[null,14,5935,0.24199999999999999,"Available"]
[null,14.5,5940,0.22,"Available"]
[null,15,5940,0.2,"Rated Power Reached"]
[null,15.5,5940,0.182,"Rated Power Reached"]
[null,16,5940,0.16600000000000001,"Rated Power Reached"]
[null,16.5,5940,0.151,"Rated Power Reached"]
[null,17,5940,0.13900000000000001,"Rated Power Reached"]
[null,17.5,5940,0.128,"Rated Power Reached"]
[null,18,5940,0.11899999999999999,"Rated Power Reached"]
[null,18.5,5940,0.112,"Rated Power Reached"]
[null,19,5940,0.105,"Rated Power Reached"]
[null,19.5,5940,0.1,"Rated Power Reached"]
[null,20,5940,9.5000000000000001E-2,"Rated Power Reached"]
[null,"Reference:"]

{"sheet":"Mode 8","index":7,"n_rows":38,"n_cols":5,"rows_kept":38,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,"Wind Speed v (m/s) for Power","Power P (kW)","Wind Speed v (m/s) for Ct","Thrust Coefficient Ct"]
[null,3,45,3,0.89200000000000002]
[null,3.5,150,3.5,0.86599999999999999]
[null,4,291,4,0.84499999999999997]
[null,4.5,465,4.5,0.83]
[null,5,674,5,0.82]
[null,5.5,921,5.5,0.81399999999999995]
[null,6,1214,6,0.80900000000000005]
[null,6.5,1559,6.5,0.8]
[null,7,1959,7,0.77700000000000002]
[null,7.5,2396,7.5,0.74199999999999999]
[null,8,2837,8,0.70099999999999996]
[null,8.5,3264,8.5,0.65600000000000003]
[null,9,3662,9,0.60899999999999999]
[null,9.5,4025,9.5,0.56200000000000006]
[null,10,4364,10,0.51500000000000001]
[null,10.5,4688,10.5,0.46800000000000003]
[null,11,4996,11,0.42299999999999999]
[null,11.5,5254,11.5,0.38200000000000001]
[null,12,5453,12,0.34599999999999997]
[null,12.5,5603,12.5,0.313]
[null,13,5710,13,0.28399999999999997]
[null,13.5,5779,13.5,0.25800000000000001]
[null,14,5813,14,0.23499999999999999]
[null,14.5,5820,14.5,0.214]
[null,15,5820,15,0.19500000000000001]
[null,15.5,5820,15.5,0.17799999999999999]
[null,16,5820,16,0.16200000000000001]
[null,16.5,5820,16.5,0.14799999999999999]
[null,17,5820,17,0.13600000000000001]
[null,17.5,5820,17.5,0.125]
[null,18,5820,18,0.11700000000000001]
[null,18.5,5820,18.5,0.109]
[null,19,5820,19,0.10299999999999999]
[null,19.5,5820,19.5,9.8000000000000004E-2]
[null,20,5820,20,9.2999999999999999E-2]

{"sheet":"Mode 9","index":8,"n_rows":50,"n_cols":5,"rows_kept":50,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct"]
[null,3,45,3,0.89200000000000002]
[null,3.5,150,3.5,0.86599999999999999]
[null,4,291,4,0.84499999999999997]
[null,4.5,465,4.5,0.83]
[null,5,674,5,0.82]
[null,5.5,921,5.5,0.81399999999999995]
[null,6,1215,6,0.79900000000000004]
[null,6.5,1555,6.5,0.76700000000000002]
[null,7,1919,7,0.72399999999999998]
[null,7.5,2277,7.5,0.67600000000000005]
[null,8,2614,8,0.624]
[null,8.5,2921,8.5,0.57199999999999995]
[null,9,3203,9,0.52]
[null,9.5,3471,9.5,0.47]
[null,10,3731,10,0.42299999999999999]
[null,10.5,3980,10.5,0.38300000000000001]
[null,11,4217,11,0.34799999999999998]
[null,11.5,4445,11.5,0.317]
[null,12,4663,12,0.28899999999999998]
[null,12.5,4845,12.5,0.26300000000000001]
[null,13,4985,13,0.24]
[null,13.5,5091,13.5,0.22]
[null,14,5169,14,0.20100000000000001]
[null,14.5,5225,14.5,0.184]
[null,15,5258,15,0.16900000000000001]
[null,15.5,5270,15.5,0.155]
[null,16,5270,16,0.14299999999999999]
[null,16.5,5270,16.5,0.13100000000000001]
[null,17,5270,17,0.122]
[null,17.5,5270,17.5,0.113]
[null,18,5270,18,0.105]
[null,18.5,5270,18.5,9.9000000000000005E-2]
[null,19,5270,19,9.2999999999999999E-2]
[null,19.5,5270,19.5,8.7999999999999995E-2]
[null,20,5270,20,8.4000000000000005E-2]
[null,20.5,5270,20.5,7.5999999999999998E-2]
[null,21,5270,21,6.8000000000000005E-2]
[null,21.5,5270,21.5,6.0999999999999999E-2]
[null,22,5270,22,5.5E-2]
[null,22.5,5270,22.5,4.9000000000000002E-2]
[null,23,5270,23,4.3999999999999997E-2]
[null,23.5,5012,23.5,3.9E-2]
[null,24,4760,24,3.5000000000000003E-2]
[null,24.5,4508,24.5,3.2000000000000001E-2]
[null,25,4264,25,2.9000000000000001E-2]
[null,25.5,4019,25.5,2.5999999999999999E-2]
[null,26,3774,26,2.5000000000000001E-2]

{"sheet":"Mode 0","index":9,"n_rows":39,"n_cols":5,"rows_kept":39,"cut":false,"hidden":false,"merged":[]}
[]
[null,"Nordex N163/6.X Wind Turbine Data"]
[]
[null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct"]
[null,3,74,3,0.874]
[null,3.5,195,3.5,0.86699999999999999]
[null,4,360,4,0.85199999999999998]
[null,4.5,567,4.5,0.83899999999999997]
[null,5,815,5,0.83]
[null,5.5,1110,5.5,0.82399999999999995]
[null,6,1458,6,0.82]
[null,6.5,1868,6.5,0.81699999999999995]
[null,7,2344,7,0.81599999999999995]
[null,7.5,2891,7.5,0.80400000000000005]
[null,8,3509,8,0.77900000000000003]
[null,8.5,4163,8.5,0.747]
[null,9,4815,9,0.70499999999999996]
[null,9.5,5437,9.5,0.65600000000000003]
[null,10,5940,10,0.60499999999999998]
[null,10.5,6304,10.5,0.55200000000000005]
[null,11,6549,11,0.5]
[null,11.5,6703,11.5,0.45]
[null,12,6780,12,0.40100000000000002]
[null,12.5,6800,12.5,0.35799999999999998]
[null,13,6800,13,0.31900000000000001]
[null,13.5,6800,13.5,0.28399999999999997]
[null,14,6800,14,0.253]
[null,14.5,6800,14.5,0.22600000000000001]
[null,15,6800,15,0.20200000000000001]
[null,15.5,6800,15.5,0.182]
[null,16,6793,16,0.16500000000000001]
[null,16.5,6752,16.5,0.15]
[null,17,6705,17,0.13600000000000001]
[null,17.5,6589,17.5,0.124]
[null,18,6453,18,0.113]
[null,18.5,6256,18.5,0.10299999999999999]
[null,19,6045,19,9.2999999999999999E-2]
[null,19.5,5855,19.5,8.5999999999999993E-2]
[null,20,5644,20,7.9000000000000001E-2]

{"sheet":"Mode 3","index":10,"n_rows":38,"n_cols":6,"rows_kept":38,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct"]
[null,null,3,74,3,0.874]
[null,null,3.5,195,3.5,0.86699999999999999]
[null,null,4,360,4,0.85199999999999998]
[null,null,4.5,567,4.5,0.83899999999999997]
[null,null,5,815,5,0.83]
[null,null,5.5,1110,5.5,0.82399999999999995]
[null,null,6,1458,6,0.82]
[null,null,6.5,1868,6.5,0.81699999999999995]
[null,null,7,2344,7,0.81200000000000006]
[null,null,7.5,2891,7.5,0.79300000000000004]
[null,null,8,3494,8,0.76400000000000001]
[null,null,8.5,4112,8.5,0.72399999999999998]
[null,null,9,4719,9,0.67500000000000004]
[null,null,9.5,5224,9.5,0.621]
[null,null,10,5590,10,0.56699999999999995]
[null,null,10.5,5836,10.5,0.51200000000000001]
[null,null,11,5987,11,0.45900000000000002]
[null,null,11.5,6056,11.5,0.40799999999999997]
[null,null,12,6070,12,0.36199999999999999]
[null,null,12.5,6070,12.5,0.32100000000000001]
[null,null,13,6070,13,0.28399999999999997]
[null,null,13.5,6070,13.5,0.251]
[null,null,14,6070,14,0.223]
[null,null,14.5,6070,14.5,0.19900000000000001]
[null,null,15,6070,15,0.17899999999999999]
[null,null,15.5,6070,15.5,0.161]
[null,null,16,6070,16,0.14599999999999999]
[null,null,16.5,6070,16.5,0.13300000000000001]
[null,null,17,6070,17,0.12]
[null,null,17.5,6070,17.5,0.11]
[null,null,18,6070,18,0.1]
[null,null,18.5,6070,18.5,9.0999999999999998E-2]
[null,null,19,6017,19,8.2000000000000003E-2]
[null,null,19.5,5855,19.5,7.5999999999999998E-2]
[null,null,20,5644,20,7.0000000000000007E-2]

{"sheet":"Mode 6","index":11,"n_rows":38,"n_cols":5,"rows_kept":38,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct"]
[null,3,74,3,0.874]
[null,3.5,195,3.5,0.86699999999999999]
[null,4,360,4,0.85199999999999998]
[null,4.5,567,4.5,0.83899999999999997]
[null,5,815,5,0.83]
[null,5.5,1110,5.5,0.82399999999999995]
[null,6,1459,6,0.82]
[null,6.5,1868,6.5,0.81399999999999995]
[null,7,2344,7,0.79300000000000004]
[null,7.5,2873,7.5,0.76200000000000001]
[null,8,3416,8,0.72299999999999998]
[null,8.5,3949,8.5,0.67800000000000005]
[null,9,4453,9,0.627]
[null,9.5,4886,9.5,0.57299999999999995]
[null,10,5202,10,0.51800000000000002]
[null,10.5,5424,10.5,0.46400000000000002]
[null,11,5566,11,0.41299999999999998]
[null,11.5,5643,11.5,0.36699999999999999]
[null,12,5670,12,0.32700000000000001]
[null,12.5,5670,12.5,0.29099999999999998]
[null,13,5670,13,0.25900000000000001]
[null,13.5,5670,13.5,0.23100000000000001]
[null,14,5670,14,0.20599999999999999]
[null,14.5,5670,14.5,0.184]
[null,15,5670,15,0.16500000000000001]
[null,15.5,5670,15.5,0.14899999999999999]
[null,16,5670,16,0.13500000000000001]
[null,16.5,5670,16.5,0.123]
[null,17,5670,17,0.111]
[null,17.5,5670,17.5,0.10100000000000001]
[null,18,5670,18,9.2999999999999999E-2]
[null,18.5,5670,18.5,8.4000000000000005E-2]
[null,19,5670,19,7.5999999999999998E-2]
[null,19.5,5665,19.5,7.0000000000000007E-2]
[null,20,5644,20,6.5000000000000002E-2]

{"sheet":"Vestas PO7","index":12,"n_rows":100,"n_cols":5,"rows_kept":100,"cut":false,"hidden":false,"merged":[]}
[null,"Vesta PO7"]
[]
[null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct"]
[null,3,32,3,0.96899999999999997]
[null,3.5,129,3.5,0.88500000000000001]
[null,4,288,4,0.83399999999999996]
[null,4.5,481,4.5,0.81799999999999995]
[null,5,715,5,0.81200000000000006]
[null,5.5,999,5.5,0.81499999999999995]
[null,6,1340,6,0.81399999999999995]
[null,6.5,1739,6.5,0.81]
[null,7,2203,7,0.80500000000000005]
[null,7.5,2729,7.5,0.79700000000000004]
[null,8,3324,8,0.78800000000000003]
[null,8.5,3986,8.5,0.77700000000000002]
[null,9,4685,9,0.75]
[null,9.5,5314,9.5,0.69]
[null,10,5904,10,0.628]
[null,10.5,6441,10.5,0.57099999999999995]
[null,11,6854,11,0.51300000000000001]
[null,11.5,7078,11.5,0.45100000000000001]
[null,12,7160,12,0.39200000000000002]
[null,12.5,7195,12.5,0.34100000000000003]
[null,13,7200,13,0.29899999999999999]
[null,13.5,7200,13.5,0.26400000000000001]
[null,14,7200,14,0.23499999999999999]
[null,14.5,7200,14.5,0.21]
[null,15,7200,15,0.188]
[null,15.5,7200,15.5,0.17]
[null,16,7200,16,0.155]
[null,16.5,7200,16.5,0.14099999999999999]
[null,17,7200,17,0.129]
[null,17.5,7194,17.5,0.11899999999999999]
[null,18,7124,18,0.108]
[null,18.5,6959,18.5,9.8000000000000004E-2]
[null,19,6789,19,8.7999999999999995E-2]
[null,19.5,6630,19.5,0.08]
[null,20,6472,20,7.2999999999999995E-2]
[null,20.5,6262,20.5,6.6000000000000003E-2]
[null,21,5946,21,5.8000000000000003E-2]
[null,21.5,5538,21.5,5.1999999999999998E-2]
[null,22,5069,22,4.4999999999999998E-2]
[null,22.5,4597,22.5,3.9E-2]
[null,23,4121,23,3.3000000000000002E-2]
[null,23.5,3636,23.5,2.8000000000000001E-2]
[null,24,3169,24,2.4E-2]
[null,24.5,2718,24.5,0.02]
[null,25,2328,25,1.7000000000000001E-2]
[null,"This table has 45 rows. The power values seem to increase to a maximum of 7200 kW and then decrease after v=17.00, which is typical for a power curve with cut-out. The thrust coefficients decrease with wind speed."]
[]
[null,"I think this is a reasonable interpretation."]
[]
[null,"So, I'll output this table."]
[]
[null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct"]
[null,3,323,3,0.96899999999999997]
[null,3.5,1293,3.5,0.88500000000000001]
[null,4,2884,4,0.83399999999999996]
[null,4.5,4814,4.5,0.81799999999999995]
[null,5,7155,5,0.81200000000000006]
[null,5.5,9995,5.5,0.81499999999999995]
[null,6,1340,6,0.81399999999999995]
[null,6.5,1739,6.5,0.81]
[null,7,2203,7,0.80500000000000005]
[null,7.5,2729,7.5,0.79700000000000004]
[null,8,3324,8,0.78800000000000003]
[null,8.5,3986,8.5,0.77700000000000002]
[null,9,4685,9,0.75]
[null,9.5,5314,9.5,0.69]
[null,10,5904,10,0.628]
[null,10.5,6441,10.5,0.57099999999999995]
[null,11,6854,11,0.51300000000000001]
[null,11.5,7078,11.5,0.45100000000000001]
[null,12,7160,12,0.39200000000000002]
[null,12.5,7195,12.5,0.34100000000000003]
[null,13,7200,13,0.29899999999999999]
[null,13.5,7200,13.5,0.26400000000000001]
[null,14,7200,14,0.23499999999999999]
[null,14.5,7200,14.5,0.21]
[null,15,7200,15,0.188]
[null,15.5,7200,15.5,0.17]
[null,16,7200,16,0.155]
[null,16.5,7200,16.5,0.14099999999999999]
[null,17,7200,17,0.129]
[null,17.5,7194,17.5,0.11899999999999999]
[null,18,7124,18,0.108]
[null,18.5,6959,18.5,9.8000000000000004E-2]
[null,19,6789,19,8.7999999999999995E-2]
[null,19.5,6630,19.5,0.08]
[null,20,6472,20,7.2999999999999995E-2]
[null,20.5,6262,20.5,6.6000000000000003E-2]
[null,21,5946,21,5.8000000000000003E-2]
[null,21.5,5538,21.5,5.1999999999999998E-2]
[null,22,5069,22,4.4999999999999998E-2]
[null,22.5,4597,22.5,3.9E-2]
[null,23,4121,23,3.3000000000000002E-2]
[null,23.5,3636,23.5,2.8000000000000001E-2]
[null,24,3169,24,2.4E-2]
[null,24.5,2718,24.5,0.02]
[null,25,2328,25,1.7000000000000001E-2]

{"sheet":"Vestas 6.1 SO1","index":13,"n_rows":99,"n_cols":5,"rows_kept":99,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,"Wind Speed (m/s)","Power (kW)","Thrust Coefficient (Ct)"]
[null,3,32,0.96899999999999997]
[null,3.5,129,0.88500000000000001]
[null,4,288,0.83099999999999996]
[null,4.5,471,0.81699999999999995]
[null,5,698,0.81200000000000006]
[null,5.5,974,0.81399999999999995]
[null,6,1307,0.81399999999999995]
[null,6.5,1697,0.81100000000000005]
[null,7,2150,0.80600000000000005]
[null,7.5,2666,0.79900000000000004]
[null,8,3251,0.79100000000000004]
[null,8.5,3903,0.77400000000000002]
[null,9,4570,0.73099999999999998]
[null,9.5,5206,0.67500000000000004]
[null,10,5774,0.61599999999999999]
[null,10.5,6100,0.55000000000000004]
[null,11,6100,0.48199999999999998]
[null,11.5,6100,0.41599999999999998]
[null,12,6100,0.36099999999999999]
[null,12.5,6100,0.314]
[null,13,6100,0.27500000000000002]
[null,13.5,6100,0.24299999999999999]
[null,14,6100,0.217]
[null,14.5,6100,0.19400000000000001]
[null,15,6100,0.17399999999999999]
[null,15.5,6100,0.158]
[null,16,6100,0.14299999999999999]
[null,16.5,5887,0.13]
[null,17,5674,0.11899999999999999]
[null,17.5,5461,0.109]
[null,18,5248,0.1]
[null,18.5,5035,9.1999999999999998E-2]
[null,19,4822,8.5000000000000006E-2]
[null,19.5,4609,7.8E-2]
[null,20,4396,7.1999999999999995E-2]
[null,20.5,4183,6.5000000000000002E-2]
[null,21,3970,5.8000000000000003E-2]
[null,21.5,3757,5.0999999999999997E-2]
[null,22,3544,4.3999999999999997E-2]
[null,22.5,3331,3.7999999999999999E-2]
[null,23,3118,3.3000000000000002E-2]
[null,23.5,2905,2.8000000000000001E-2]
[null,24,2692,2.4E-2]
[null,24.5,2479,0.02]
[null,25,2266,1.7000000000000001E-2]
[]
[null,"I think this is a reasonable interpretation."]
[]
[null,"So, I'll output this table."]
[]
[null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct"]
[null,3,323,3,0.96899999999999997]
[null,3.5,1293,3.5,0.88500000000000001]
[null,4,2884,4,0.83399999999999996]
[null,4.5,4814,4.5,0.81799999999999995]
[null,5,7155,5,0.81200000000000006]
[null,5.5,9995,5.5,0.81499999999999995]
[null,6,1340,6,0.81399999999999995]
[null,6.5,1739,6.5,0.81]
[null,7,2203,7,0.80500000000000005]
[null,7.5,2729,7.5,0.79700000000000004]
[null,8,3324,8,0.78800000000000003]
[null,8.5,3986,8.5,0.77700000000000002]
[null,9,4685,9,0.75]
[null,9.5,5314,9.5,0.69]
[null,10,5904,10,0.628]
[null,10.5,6441,10.5,0.57099999999999995]
[null,11,6854,11,0.51300000000000001]
[null,11.5,7078,11.5,0.45100000000000001]
[null,12,7160,12,0.39200000000000002]
[null,12.5,7195,12.5,0.34100000000000003]
[null,13,7200,13,0.29899999999999999]
[null,13.5,7200,13.5,0.26400000000000001]
[null,14,7200,14,0.23499999999999999]
[null,14.5,7200,14.5,0.21]
[null,15,7200,15,0.188]
[null,15.5,7200,15.5,0.17]
[null,16,7200,16,0.155]
[null,16.5,7200,16.5,0.14099999999999999]
[null,17,7200,17,0.129]
[null,17.5,7194,17.5,0.11899999999999999]
[null,18,7124,18,0.108]
[null,18.5,6959,18.5,9.8000000000000004E-2]
[null,19,6789,19,8.7999999999999995E-2]
[null,19.5,6630,19.5,0.08]
[null,20,6472,20,7.2999999999999995E-2]
[null,20.5,6262,20.5,6.6000000000000003E-2]
[null,21,5946,21,5.8000000000000003E-2]
[null,21.5,5538,21.5,5.1999999999999998E-2]
[null,22,5069,22,4.4999999999999998E-2]
[null,22.5,4597,22.5,3.9E-2]
[null,23,4121,23,3.3000000000000002E-2]
[null,23.5,3636,23.5,2.8000000000000001E-2]
[null,24,3169,24,2.4E-2]
[null,24.5,2718,24.5,0.02]
[null,25,2328,25,1.7000000000000001E-2]

{"sheet":"Vestas 5.2 SO2","index":14,"n_rows":48,"n_cols":5,"rows_kept":48,"cut":false,"hidden":false,"merged":[]}
[]
[]
[null,"Wind Speed v (m/s)","Power P (kW)","Wind Speed v (m/s)","Thrust Coefficient Ct"]
[null,3,32,3,0.96899999999999997]
[null,3.5,129,3.5,0.88500000000000001]
[null,4,288,4,0.83199999999999996]
[null,4.5,471,4.5,0.81599999999999995]
[null,5,697,5,0.81200000000000006]
[null,5.5,974,5.5,0.81399999999999995]
[null,6,1307,6,0.81399999999999995]
[null,6.5,1697,6.5,0.81100000000000005]
[null,7,2151,7,0.80600000000000005]
[null,7.5,2668,7.5,0.79900000000000004]
[null,8,3227,8,0.78700000000000003]
[null,8.5,3780,8.5,0.747]
[null,9,4301,9,0.69099999999999995]
[null,9.5,4787,9.5,0.63200000000000001]
[null,10,5200,10,0.57499999999999996]
[null,10.5,5200,10.5,0.51400000000000001]
[null,11,5200,11,0.45100000000000001]
[null,11.5,5200,11.5,0.39200000000000002]
[null,12,5200,12,0.34200000000000003]
[null,12.5,5200,12.5,0.3]
[null,13,5200,13,0.26400000000000001]
[null,13.5,5200,13.5,0.23400000000000001]
[null,14,5200,14,0.20799999999999999]
[null,14.5,5200,14.5,0.186]
[null,15,5200,15,0.16700000000000001]
[null,15.5,5200,15.5,0.15]
[null,16,5200,16,0.13700000000000001]
[null,16.5,5020,16.5,0.124]
[null,17,4839,17,0.113]
[null,17.5,4659,17.5,0.104]
[null,18,4479,18,9.6000000000000002E-2]
[null,18.5,4298,18.5,8.7999999999999995E-2]
[null,19,4118,19,8.1000000000000003E-2]
[null,19.5,3938,19.5,7.4999999999999997E-2]
[null,20,3757,20,7.0000000000000007E-2]
[null,20.5,3577,20.5,6.4000000000000001E-2]
[null,21,3397,21,5.8000000000000003E-2]
[null,21.5,3216,21.5,5.0999999999999997E-2]
[null,22,3036,22,4.3999999999999997E-2]
[null,22.5,2856,22.5,3.7999999999999999E-2]
[null,23,2675,23,3.3000000000000002E-2]
[null,23.5,2495,23.5,2.8000000000000001E-2]
[null,24,2315,24,2.4E-2]
[null,24.5,2134,24.5,0.02]
[null,25,1954,25,1.7000000000000001E-2]

{"sheet":"Vestas 4.8 SO4","index":15,"n_rows":49,"n_cols":5,"rows_kept":49,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[null,"v (m/s)","P (kW)","v (m/s)","ct"]
[null,3,32,3,0.96899999999999997]
[null,3.5,129,3.5,0.88500000000000001]
[null,4,288,4,0.83099999999999996]
[null,4.5,471,4.5,0.81599999999999995]
[null,5,697,5,0.81200000000000006]
[null,5.5,974,5.5,0.81399999999999995]
[null,6,1307,6,0.81399999999999995]
[null,6.5,1697,6.5,0.81100000000000005]
[null,7,2151,7,0.80400000000000005]
[null,7.5,2650,7.5,0.77900000000000003]
[null,8,3149,8,0.72]
[null,8.5,3619,8.5,0.65300000000000002]
[null,9,4065,9,0.59299999999999997]
[null,9.5,4470,9.5,0.53900000000000003]
[null,10,4800,10,0.48899999999999999]
[null,10.5,4800,10.5,0.439]
[null,11,4800,11,0.39100000000000001]
[null,11.5,4800,11.5,0.34399999999999997]
[null,12,4800,12,0.30299999999999999]
[null,12.5,4800,12.5,0.26800000000000002]
[null,13,4800,13,0.23699999999999999]
[null,13.5,4800,13.5,0.21]
[null,14,4800,14,0.187]
[null,14.5,4800,14.5,0.16800000000000001]
[null,15,4800,15,0.151]
[null,15.5,4800,15.5,0.13600000000000001]
[null,16,4800,16,0.123]
[null,16.5,4637,16.5,0.112]
[null,17,4474,17,0.10199999999999999]
[null,17.5,4311,17.5,9.5000000000000001E-2]
[null,18,4147,18,8.6999999999999994E-2]
[null,18.5,3984,18.5,0.08]
[null,19,3821,19,7.3999999999999996E-2]
[null,19.5,3658,19.5,6.8000000000000005E-2]
[null,20,3495,20,6.3E-2]
[null,20.5,3332,20.5,5.8999999999999997E-2]
[null,21,3168,21,5.5E-2]
[null,21.5,3005,21.5,0.05]
[null,22,2842,22,4.3999999999999997E-2]
[null,22.5,2679,22.5,3.7999999999999999E-2]
[null,23,2516,23,3.3000000000000002E-2]
[null,23.5,2353,23.5,2.8000000000000001E-2]
[null,24,2189,24,2.4E-2]
[null,24.5,2026,24.5,0.02]
[null,25,1863,25,1.7000000000000001E-2]

{"sheet":"Enercon Mode 0","index":16,"n_rows":30,"n_cols":5,"rows_kept":30,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[null,"Wind Speed v (m/s) for Power","Power P (kW)","Wind Speed v (m/s) for Ct","Thrust Coefficient Ct"]
[null,1,1,1,0]
[null,2,3,2,0.78100000000000003]
[null,3,25,3,0.78500000000000003]
[null,4,82,4,0.77400000000000002]
[null,5,174,5,0.78100000000000003]
[null,6,321,6,0.77700000000000002]
[null,7,532,7,0.77800000000000002]
[null,8,815,8,0.77500000000000002]
[null,9,1180,9,0.76900000000000002]
[null,10,1580,10,0.77]
[null,11,1810,11,0.77300000000000002]
[null,12,1980,12,0.495]
[null,13,2050,13,0.36699999999999999]
[null,14,2050,14,0.28599999999999998]
[null,15,2050,15,0.23]
[null,16,2050,16,0.188]
[null,17,2050,17,0.156]
[null,18,2050,18,0.13100000000000001]
[null,19,2050,19,0.111]
[null,20,2050,20,9.6000000000000002E-2]
[null,21,2050,21,8.4000000000000005E-2]
[null,22,2050,22,7.3999999999999996E-2]
[null,23,2050,23,6.6000000000000003E-2]
[null,24,2050,24,5.8999999999999997E-2]
[null,25,2050,25,5.2999999999999999E-2]

{"sheet":"Enercon 2","index":17,"n_rows":54,"n_cols":5,"rows_kept":54,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[null,"v (m/s)","P_v (kW)","P_v (kW)","C_t"]
[null,0,0,0,0]
[null,0.5,0,0,0]
[null,1,0,0,0]
[null,1.5,0,0,0.77]
[null,2,0,0,0.78]
[null,2.5,10,10,0.78]
[null,3,25,25,0.77]
[null,3.5,49,49,0.77]
[null,4,82,82,0.78]
[null,4.5,123,123,0.78]
[null,5,174,174,0.78]
[null,5.5,240,240,0.78]
[null,6,321,321,0.78]
[null,6.5,418,418,0.78]
[null,7,532,532,0.77]
[null,7.5,664,664,0.77]
[null,8,815,815,0.77]
[null,8.5,988,988,0.77]
[null,9,1180,1180,0.77]
[null,9.5,1384,1384,0.77]
[null,10,1580,1580,0.77]
[null,10.5,1749,1749,0.77]
[null,11,1890,1890,0.61]
[null,11.5,2005,2005,0.51]
[null,12,2100,2100,0.43]
[null,12.5,2180,2180,0.38]
[null,13,2250,2250,0.33]
[null,13.5,2311,2311,0.3]
[null,14,2350,2350,0.27]
[null,14.5,2350,2350,0.24]
[null,15,2350,2350,0.22]
[null,15.5,2350,2350,0.2]
[null,16,2350,2350,0.18]
[null,16.5,2350,2350,0.16]
[null,17,2350,2350,0.15]
[null,17.5,2350,2350,0.14000000000000001]
[null,18,2350,2350,0.13]
[null,18.5,2350,2350,0.12]
[null,19,2350,2350,0.11]
[null,19.5,2350,2350,0.1]
[null,20,2350,2350,0.1]
[null,20.5,2350,2350,0.09]
[null,21,2350,2350,0.08]
[null,21.5,2350,2350,0.08]
[null,22,2350,2350,7.0000000000000007E-2]
[null,22.5,2350,2350,7.0000000000000007E-2]
[null,23,2350,2350,0.06]
[null,23.5,2346,2346,0.06]
[null,24,2339,2339,0.06]
[null,24.5,2350,2350,0.05]